## Current Draw
Use yellow cells to enter quantities and current values.
Select devices using the "Qty" column.
Use the drop downs to select parts for NAC circuits.
To clear selected devices, click the "Clear Quantities" button.
System Current Draw | [9 empty] | Qty
7100 Series Control Panel with Broadband
> 0
| Total Standby |  |  | 0 | Total Alarm |  |  | 0
| Standby Current |  |  |  | Alarm Current
Device | Qty |  | Draw | Standby | Qty |  | Draw | Alarm
1. System (Please only select one)
Basic System Module, 2 SLC | 0 | x | 0.065 |  | 0 | x | 0.085
Basic System Module, 1 SLC with DACT | 0 | x | 0.075 |  | 0 | x | 0.095
Basic System Module, 2 SLC with DACT | 0 | x | 0.085 |  | 0 | x | 0.105
2. 7100 Optional Modules
Printer Transient Module (PTRM) | 0 | x | 0.02 |  | 0 | x | 0.02
Class A Option Module (CAOM) | 0 | x | 0.001 |  | 0 | x | 0.001
Municipal Circuit Option Module (MCOM) | 0 | x | 0.001 |  | 0 | x | 0.001
Optional Remote Serial Annunicator (LCD-7100) | 0 | x | 0.05 |  | 0 | x | 0.075
Remote LED Driver Module (LDM-7100) | 0 | x | 0.035 |  | 0 | x | 0.2
Intelligent Network Interface Module - Copper Wire (INI-7100-UTP) | 0 | x | 0.04 |  | 0 | x | 0.04
Intelligent Network Interface Module - Fiber Optic (INI-7100-FO) | 0 | x | 0.04 |  | 0 | x | 0.04
3. INI-VGC BroadBand Components
Intelligent Network Voice Gateway-Command Center (INI-VGC) | 0 | x | 0.15 |  | 0 | x | 0.15
Addressable Switch Sub-assembly (ASM-16) | 0 | x | 0.011 |  | 0 | x | 0.011
Voice Paging Microphone (Microphone) | 0 | x | 0.001 |  | 0 | x | 0.001
Fire Fighter's Telephone Handset | 0 | x | 0.02 |  | 0 | x | 0.02
Addressable Output Module-Telephone (AOM-TEL) | 0 | x | 0.002 |  | 0 | x | 0.065
4. PM-9 BroadBand Components
INX Power Supply Sub-assembly, 9 Amp (PM-9) | 0 | x | 0.05 |  | 0 | x | 0.05
Intelligent Network, Voice Gateway (INI-VGX) | 0 | x | 0.15 |  | 0 | x | 0.15
Amplifier Sub-assembly, 50 watt (AM-50) | 0 | x | 0.12 |  | 0 | x | 2.206
Addressable Switch Sub-assembly (ASM-16) | 0 | x | 0.011 |  | 0 | x | 0.011
Addressable Output Module-Telephone (AOM-TEL) | 0 | x | 0.002 |  | 0 | x | 0.0065
Addressable Output Module-Multiplex (AOM-MUX) | 0 | x | 0.004 |  | 0 | x | 0.0065
5. Two-Wire Smoke Detectors
Two-wire Smoke Detector 1 | 0 | x | 0 |  | 0 | x | 0
Two-wire Smoke Detector 2 | 0 | x | 0 |  | 0 | x | 0
Two-wire Smoke Detector 3 | 0 | x | 0 |  | 0 | x | 0
Two-wire Smoke Detector 4 | 0 | x | 0 |  | 0 | x | 0
6. Four-Wire Smoke Detectors
Four-wire Smoke Detector 1 | 0 | x | 0 |  | 0 | x | 0
Four-wire Smoke Detector 2 | 0 | x | 0 |  | 0 | x | 0
Four-wire Smoke Detector 3 | 0 | x | 0 |  | 0 | x | 0
Four-wire Smoke Detector 4 | 0 | x | 0 |  | 0 | x | 0
7. Notification Appliances
| 0 | x | 0 |  | 0 | x | 0 |  | 1
| 0 | x | 0 |  | 0 | x | 0 |  | 1
| 0 | x | 0 |  | 0 | x | 0 |  | 1
| 0 | x | 0 |  | 0 | x | 0 |  | 1
| 0 | x | 0 |  | 0 | x | 0 |  | 1
| 0 | x | 0 |  | 0 | x | 0 |  | 1
| 0 | x | 0 |  | 0 | x | 0 |  | 1
| 0 | x | 0 |  | 0 | x | 0 |  | 1
| 0 | x | 0 |  | 0 | x | 0 |  | 1
| 0 | x | 0 |  | 0 | x | 0 |  | 1
| 1 | Total Standby Load: |  | 0 |  | Total Alarm Load: |  | 0
1
Note on G12: Standby -- The system is operating from normal AC line power. All input and output circuits are "normal" (no alarm or trouble conditions).
Note on G15: Select only 1 Main System Device.
Note on G16: Select only 1 Main System Device.
Note on G17: Select only 1 Main System Device.
Note on I28: Add 0.003A for each LED that is programmed to be lit for trouble or supervisory off-normal conditions
Note on I36: Add 0.003A for each Led programmed to be lit during Supervisory or Alarm condition.
Note on K12: Alarm -- The system in alarm when any analog/addressable initiation device reports an alarm condition. Red LED.
Note on M28: Add 0.003A for each each LED that is programmed to be lit for alarm conditions
Note on M36: Add 0.003A for each Led programmed to be lit during Supervisory or Alarm condition.

## Battery Size
System Power Requirements
7100 Fire Alarm Control Panel with Broadband
Protected Premises: |  |  |  | Date:
Address:
City: |  | State: |  | Zip:
Prepared By: |  |  |  | Phone:
Address: |  |  | Email:
City: |  | State: |  | Zip:
Secondary Load Requirements |  | 0 | Amp Hours
Total Secondary Load from the calculation table below.
Current Draw |  |  | Time (hours) |  | Total (AH)
Secondary Standby Load |  | x | Required Standby Time
0 |  |  | 24 |  | 0
Secondary Alarm Load |  | x | Required Alarm Time (hours)
0 |  |  | 0.084 |  | 0
Total Secondary Load |  |  |  |  | 0
Derating factor |  |  |  |  | 1.2
Secondary Load Requirements |  |  |  |  | 0
Battery Selection |  | 7 | Amp Hours
Select batteries from the list below.
7.0 AH Battery (12 volt)
Battery Distribution Chart
Shows amp-hour distribution of your selections.
Spare Battery Capacity | 7
Secondary Standby Load | 0
Secondary Alarm Load | 0
Comments
1. Batteries will fit in the FACP cabinet.
2. Selected battery size meets secondary load requirements.
7.0 AH Battery (12 volt)
17 AH Battery (12 volt)
31 AH Battery (12 volt)
55 AH Battery (12 volt)
Note on C18: Total Standby Load from Current Draw sheet.
Note on C20: Total Primary Alarm Load from Current Draw sheet.
Note on C29: Click to select batteries from dropdown list.
Note on G20: Double-click this cell to input the amp hours in minutes.
Note on I22: Click to change the default derating (safety) factor of 1.2.

## Devices
User Defined -- Use rows 2-16 to create a new part so it will appear in the NAC dropdown box (Current Draw sheet). If you need additional User-Defined rows, copy and paste a new row.
Tip -- Copy frequently used parts into a User Defined row to minimize scrolling in the dropdown box.
Notification Appliances
Item | Part Number | Part Name | Standby | Alarm | TYPE
1 |  | DO NOT DELETE THIS LINE | 0 | 0 | NO DELETE
2 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
3 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
4 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
5 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
6 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
7 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
8 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
9 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
10 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
11 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
12 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
13 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
14 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
15 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
16 | User Defined | <Enter Description here> | 0 | 0 | <Enter Type>
17 | A10 | A10 VIBRATONE GONG | 0 | 0.4 | Bell
18 | AH-24-R | Horn, 24 VDC | 0 | 0.041 | Horn
19 | AH-24WP-R | Horn, 24 VDC | 0 | 0.041 | Horn
20 | AS-24100C-FW | Horn Strobe, 24 VDC, 100 cd | 0 | 0.425 | Horn/Strobe
21 | AS-24110MCW-FR | Horn Strobe, 24 volt, red, Selectable, 110 candela | 0 | 0.324 | Horn/Strobe
22 | AS-24110MCW-FW | Horn Strobe, 24 volt, white, Selectable, 110 candela | 0 | 0.324 | Horn/Strobe
23 | AS-24110W-FR | Horn Strobe, 24 VDC, 110 cd | 0 | 0.306 | Horn/Strobe
24 | AS-241575W-FR | Horn Strobe, 24 VDC, 15/75 cd | 0 | 0.13 | Horn/Strobe
25 | AS-2415MCW-FR | Horn Strobe, 24 volt, red, Selectable, 15 Candela | 0 | 0.1 | Horn/Strobe
26 | AS-2415MCW-FW | Horn Strobe, 24 volt, white, Selectable, 15 candela | 0 | 0.1 | Horn/Strobe
27 | AS-2415W-FR | Horn Strobe, 24 VDC, 15 cd | 0 | 0.109 | Horn/Strobe
28 | AS-2430MCW-FR | Horn Strobe, 24 volt, red, Selectable, 30 candela | 0 | 0.149 | Horn/Strobe
29 | AS-2430MCW-FW | Horn Strobe, 24 volt, white, Selectable, 30 candela | 0 | 0.149 | Horn/Strobe
30 | AS-2430W-FR | Horn Strobe, 24 VDC, 30 cd | 0 | 0.16 | Horn/Strobe
31 | AS-2475C-FW | Horn Strobe, 24 VDC, 75 cd | 0 | 0.376 | Horn/Strobe
32 | AS-2475MCW-FR | Horn Strobe, 24 volt, red, Selectable, 75 candela | 0 | 0.255 | Horn/Strobe
33 | AS-2475MCW-FW | Horn Strobe, 24 volt, white, Selectable, 75 candela | 0 | 0.255 | Horn/Strobe
34 | AS-2475W-FR | Horn Strobe, 24 VDC, 75 cd | 0 | 0.253 | Horn/Strobe
35 | ASWP-2475W | Audible Strobe Weatherproof 75cd | 0 | 0.161 | Speaker/Strobe
36 | AVS44 | Synchronization Module, GOT/GOS Series Only | 0 | 0 | Sync Module
37 | CH1224 | Chime, 12/24 VDC, red, wall mount | 0 | 0.07 | Chime
38 | CH1224W | Chime, 12/24 VDC, white, wall mount | 0 | 0.07 | Chime
39 | CH24110 | Chime, 24 VDC, 110cd | 0 | 0.209 | Chime
40 | CH2415 | Chime, 24 VDC, 15cd | 0 | 0.059 | Chime
41 | CH241575 | Chime, 24 VDC, 15/75cd | 0 | 0.069 | Chime
42 | CH2430 | Chime, 24 VDC, 30cd | 0 | 0.09 | Chime
43 | CH2475 | Chime, 24 VDC, 75cd | 0 | 0.16 | Chime
44 | CH70-24110MCW-FR | Chime Strobe, 24 VDC, 110 cd, red | 0 | 0.289 | Chime
45 | CH70-24110MCW-FW | Chime Strobe, 24 VDC, 110 cd, white | 0 | 0.289 | Chime
46 | CH70-241575W-FR | Chime, 24 VDC, 15/75 cd | 0 | 0.085 | Chime
47 | CH70-2415MCW-FR | Chime Strobe, 24 VDC, 15 cd, red | 0 | 0.07 | Chime
48 | CH70-2415MCW-FW | Chime Strobe, 24 VDC, 15 cd, white | 0 | 0.07 | Chime
49 | CH70-2415W-FR | Chime, 24 VDC, 15 cd | 0 | 0 | Chime
50 | CH70-2430MCW-FR | Chime Strobe, 24 VDC, 30 cd, red | 0 | 0.114 | Chime
51 | CH70-2430MCW-FW | Chime Strobe, 24 VDC, 30 cd, white | 0 | 0.114 | Chime
52 | CH70-2430W-FR | Chime, 24 VDC, 30 cd | 0 | 0 | Chime
53 | CH70-2475MCW-FR | Chime Strobe, 24 VDC, 75 cd, red | 0 | 0.22 | Chime
54 | CH70-2475MCW-FW | Chime Strobe, 24 VDC, 75 cd, white | 0 | 0.22 | Chime
55 | CH70-2475W-FR | Chime, 24 VDC, 75 cd | 0 | 0.153 | Chime
56 | CH70-24-R | Chime, 24 VDC | 0 | 0 | Chime
57 | CH90-24-W | Chime, 24 VDC | 0 | 0 | Chime
58 | CHR | Chime, red | 0 | 0.058 | Chime
59 | CHSR110 | 2-Wire Chime/Strobe 110 cd, red | 0 | 0.21 | Chime/Strobe
60 | CHSR115 | 2-Wire Chime/Strobe 115 cd, red | 0 | 0.217 | Chime/Strobe
61 | CHSR15 | 2-Wire Chime/Strobe 15 cd, red | 0 | 0.07 | Chime/Strobe
62 | CHSR1575 | 2-Wire Chime/Strobe 15/75 cd, red | 0 | 0.081 | Chime/Strobe
63 | CHSR30 | 2-Wire Chime/Strobe 30 cd, red | 0 | 0.099 | Chime/Strobe
64 | CHSR75 | 2-Wire Chime/Strobe 75 cd, red | 0 | 0.165 | Chime/Strobe
65 | CHSR95 | 2-Wire Chime/Strobe 95 cd, red | 0 | 0.189 | Chime/Strobe
66 | CHSW110 | 2-Wire Chime/Strobe 110 cd, white | 0 | 0.21 | Chime/Strobe
67 | CHSW115 | 2-Wire Chime/Strobe 115 cd, white | 0 | 0.217 | Chime/Strobe
68 | CHSW15 | 2-Wire Chime/Strobe 15 cd, white | 0 | 0.07 | Chime/Strobe
69 | CHSW1575 | 2-Wire Chime/Strobe 15/75 cd, white | 0 | 0.081 | Chime/Strobe
70 | CHSW30 | 2-Wire Chime/Strobe 30 cd, white | 0 | 0.099 | Chime/Strobe
71 | CHSW75 | 2-Wire Chime/Strobe 75 cd, white | 0 | 0.165 | Chime/Strobe
72 | CHSW95 | 2-Wire Chime/Strobe 95 cd, white | 0 | 0.189 | Chime/Strobe
73 | CHW | Chime, white | 0 | 0.058 | Chime
74 | DSM-12/24-R | Sync Module | 0 | 0.038 | Sync Module
75 | E70-24110W-FR | Speaker Strobe, 24 VDC, 110 cd, 25/70.7 Vrms | 0 | 0.276 | Speaker/Strobe
76 | E70-241575W-FR | Speaker Strobe, 24 VDC, 15/75 cd, 25/70.7 Vrms | 0 | 0.08 | Speaker/Strobe
77 | E70-2415W-FR | Speaker Strobe, 24 VDC, 15 cd, 25/70.7 Vrms | 0 | 0.072 | Speaker/Strobe
78 | E70-24185W-FR | Speaker Strobe, 24 VDC, 185 cd, 25/70.7 Vrms | 0 | 0.293 | Speaker/Strobe
79 | E70-2430W-FR | Speaker Strobe, 24 VDC, 30 cd, 25/70.7 Vrms | 0 | 0.125 | Speaker/Strobe
80 | E70-2475W-FR | Speaker Strobe, 24 VDC, 75 cd, 25/70.7 Vrms | 0 | 0.215 | Speaker/Strobe
81 | E70-R | Speaker, 25 or 70.7 Vrms, 1/8 to 2 watts | 0 | 0 | Speaker
82 | E70-W | Speaker, 25 or 70.7 Vrms, 1/8 to 2 watts | 0 | 0 | Speaker
83 | E90-24100C-FW | Speaker Strobe, 24 VDC, 100, 25/70.7 Vrms | 0 | 0.375 | Speaker/Strobe
84 | E90-2415C-FW | Speaker Strobe, 24 VDC, 15 cd, 25/70.7 Vrms | 0 | 0.105 | Speaker/Strobe
85 | E90-2430C-FW | Speaker Strobe, 24 VDC, 75 cd, 25/70.7 Vrms | 0 | 0.158 | Speaker/Strobe
86 | E90-2475C-FW | Speaker Strobe, 24 VDC, 75 cd, 25/70.7 Vrms | 0 | 0.33 | Speaker/Strobe
87 | E90-R | Speaker, 25 or 70.7 Vrms, 1/8 to 2 watts | 0 | 0 | Speaker
88 | E90-W | Speaker, 25 or 70.7 Vrms, 1/8 to 2 watts | 0 | 0 | Speaker
89 | ET-1010-R | Speaker, 1/8 to 8 watts | 0 | 0 | Speaker
90 | ET-1080-IS-24-R | Speaker Strobe, 75 cd | 0 | 0.245 | Speaker/Strobe
91 | ET-1080-LS-24-R | Speaker Strobe, 15 cd | 0 | 0.08 | Speaker/Strobe
92 | ET-1080-LSM-24R | Speaker Strobe, 15/75 cd | 0 | 0.115 | Speaker/Strobe
93 | ET-1080-MS-24-R | Speaker Strobe, 30 cd | 0 | 0.135 | Speaker/Strobe
94 | ET-1080-R | Speaker, 1/8 to 8 watts | 0 | 0 | Speaker
95 | ET70-24110MCW-FR | Speaker Strobe, wall, 24 VDC, red, sel cd 110 candela | 0 | 0.289 | Speaker/Strobe
96 | ET70-24110MCW-FW | Speaker Strobe, wall, 24 VDC, white, sel cd 110 candela | 0 | 0.289 | Speaker/Strobe
97 | ET70-24110W-FR | Speaker Strobe, 24 VDC, 110 cd, 25/70.7 Vrms, flush, square, | 0 | 0.276 | Speaker/Strobe
98 | ET70-241575W-FR | Speaker Strobe, 24 VDC, 15/75 cd, 25/70.7 Vrms | 0 | 0.099 | Speaker/Strobe
99 | ET70-2415MCW-FR | Speaker Strobe, wall, 24 VDC, red, sel cd 15 candela | 0 | 0.07 | Speaker/Strobe
100 | ET70-2415MCW-FW | Speaker Strobe, wall, 24 VDC, white, sel cd 15 candela | 0 | 0.07 | Speaker/Strobe
101 | ET70-2415W-FR | Speaker Strobe, 24 VDC, 15 cd, 25/70.7 Vrms | 0 | 0.072 | Speaker/Strobe
102 | ET70-2430MCW-FR | Speaker Strobe, wall, 24 VDC, red, sel cd 30 candela | 0 | 0.114 | Speaker/Strobe
103 | ET70-2430MCW-FW | Speaker Strobe, wall, 24 VDC, white, sel cd 30 candela | 0 | 0.114 | Speaker/Strobe
104 | ET70-2475MCW-FR | Speaker Strobe, wall, 24 VDC, red, sel cd 75 candela | 0 | 0.22 | Speaker/Strobe
105 | ET70-2475MCW-FW | Speaker Strobe, wall, 24 VDC, white, sel cd 75 candela | 0 | 0.22 | Speaker/Strobe
106 | ET70-2475W-FR | Speaker Strobe, 24 VDC, 75 cd, 25/70.7 Vrms | 0 | 0.215 | Speaker/Strobe
107 | ET70-R | Speaker, 1/8 to 8 watts | 0 | 0 | Speaker
108 | ET70-W | Speaker, 1/8 to 8 watts | 0 | 0 | Speaker
109 | ET90-24100C-FW | Speaker Strobe, 24 VDC, 100 cd, 25/70.7 Vrms | 0 | 0.375 | Speaker/Strobe
110 | ET90-2415C-FW | Speaker Strobe, 24 VDC, 15 cd, 25/70.7 Vrms | 0 | 0.105 | Speaker/Strobe
111 | ET90-2430C-FW | Speaker Strobe, 24 VDC, 30 cd, 25/70.7 Vrms | 0 | 0.158 | Speaker/Strobe
112 | ET90-2475C-FW | Speaker Strobe, 24 VDC, 75 cd, 25/70.7 Vrms | 0 | 0.33 | Speaker/Strobe
113 | ET90-W | Speaker, 25 or 70.7 Vrms, 1/8 to 8 watts | 0 | 0 | Speaker
114 | FB2PST | FIREBALL 2 STROBE WARNING LIGHT | 0 | 0.7 | Strobe
115 | GEC24-110WR | Horn Strobe, 24 VDC, Red, 110 candela | 0 | 0.147 | Horn/Strobe
116 | GEC24-110WW | Horn Strobe, 24 VDC, white, 110 candela | 0 | 0.147 | Horn/Strobe
117 | GEC24-15/75WR | Horn Strobe, 24 VDC, Red, 15/75 candela | 0 | 0.086 | Horn/Strobe
118 | GEC24-15/75WW | Horn Strobe, 24 VDC, white, 15/75 candela | 0 | 0.086 | Horn/Strobe
119 | GEC24-15WR | Horn Strobe, 24 VDC, Red, 15 candela | 0 | 0.073 | Horn/Strobe
120 | GEC24-15WW | Horn Strobe, 24 VDC, white, 15 candela | 0 | 0.073 | Horn/Strobe
121 | GEC24-30WR | Horn Strobe, 24 VDC, Red, 30 candela | 0 | 0.086 | Horn/Strobe
122 | GEC24-30WW | Horn Strobe, 24 VDC, white, 30 candela | 0 | 0.086 | Horn/Strobe
123 | GEC24-60WR | Horn Strobe, 24 VDC, Red, 60 candela | 0 | 0.115 | Horn/Strobe
124 | GEC24-60WW | Horn Strobe, 24 VDC, white, 60 candela | 0 | 0.115 | Horn/Strobe
125 | GEC24-75WR | Horn Strobe, 24 VDC, Red, 75 candela | 0 | 0.124 | Horn/Strobe
126 | GEC24-75WW | Horn Strobe, 24 VDC, white, 75 candela | 0 | 0.124 | Horn/Strobe
127 | GEH24-R | Horn, 24 Vdc, Red | 0 | 0.034 | Horn
128 | GEH24-W | Horn, 24 Vdc, White | 0 | 0.034 | Horn
129 | GES24-110WR | Strobe, 24 VDC, red, 110 candela | 0 | 0.128 | Strobe
130 | GES24-110WW | Strobe, 24 VDC, white, 110 candela | 0 | 0.128 | Strobe
131 | GES24-15/75WR | Strobe, 24 VDC, red, 15/75 candela | 0 | 0.067 | Strobe
132 | GES24-15/75WW | Strobe, 24 VDC, white, 15/75 candela | 0 | 0.067 | Strobe
133 | GES24-15WR | Strobe, 24 VDC, red, 15 candela | 0 | 0.054 | Strobe
134 | GES24-15WW | Strobe, 24 VDC, white, 15 candela | 0 | 0.054 | Strobe
135 | GES24-30WR | Strobe, 24 VDC, red, 30 candela | 0 | 0.067 | Strobe
136 | GES24-30WW | Strobe, 24 VDC, white, 30 candela | 0 | 0.067 | Strobe
137 | GES24-60WR | Strobe, 24 VDC, red, 60 candela | 0 | 0.096 | Strobe
138 | GES24-60WW | Strobe, 24 VDC, white, 60 candela | 0 | 0.096 | Strobe
139 | GES24-75WR | Strobe, 24 VDC, red, 75 candela | 0 | 0.105 | Strobe
140 | GES24-75WW | Strobe, 24 VDC, white, 75 candela | 0 | 0.105 | Strobe
141 | GMH24R | Horn, mechanical, 24 VDC | 0 | 0.033 | Horn
142 | GMS24-110WR | Horn Strobe, 24 VDC, 110 cd, ADA/UL1971 | 0 | 0.273 | Horn/Strobe
143 | GMS24-15/75CR | Horn Strobe, 24 VDC, 1575 cd | 0 | 0.163 | Horn/Strobe
144 | GMS24-15/75WR | Horn Strobe, 24 VDC, 15/75 cd, ADA/UL1971 | 0 | 0.138 | Horn/Strobe
145 | GMS24-15/75WRZ | Horn Strobe, 24 VDC, 15/75, ADA/UL1971 | 0 | 0.177 | Horn/Strobe
146 | GMS24-15WR | Horn Strobe, 24 VDC, 15 cd, ADA/UL1971 | 0 | 0.119 | Horn/Strobe
147 | GMS24-30/75WR | Horn Strobe, 24 VDC, 30/75 cd, ADA/UL1971 | 0 | 0.198 | Horn/Strobe
148 | GMS24-30WR | Horn Strobe, 24 VDC, red, 30 candela | 0 | 0.143 | Horn/Strobe
149 | GMS24-60WR | Horn Strobe, 24 VDC, red, 60 candela | 0 | 0.168 | Horn/Strobe
150 | GX90-4R | Mini-sounder, 24 VDC, 85 dB | 0 | 0.012 | Horn
151 | GX90-4W | Mini-sounder, 24 VDC, 85 dB | 0 | 0.012 | Horn
152 | GX90S-4-110WR | Mini-sounder Strobe, 110 cd, 24 VDC | 0 | 0.248 | Horn/Strobe
153 | GX90S-4-110WW | Mini-sounder Strobe, 110 cd, 24v | 0 | 0.248 | Horn/Strobe
154 | GX90S-4-15/75CR | Sounder Strobe, 24 VDC, 15/75 cd | 0 | 0.138 | Horn/Strobe
155 | GX90S-4-15/75CW | Sounder Strobe, 24 VDC, 15/75 cd | 0 | 0.138 | Horn/Strobe
156 | GX90S-4-15/75WW | Sounder Strobe, 24 VDC, 15 (UL1971)/75 (UL1638) cd | 0 | 0.113 | Horn/Strobe
157 | GX90S-4-1575WWZ | Horn Strobe, 24 VDC, 15/75 cd | 0 | 0.152 | Horn/Strobe
158 | GX90S-4-15WR | Sounder Strobe, 24 VDC, 15 cd, UL1971 | 0 | 0.094 | Horn/Strobe
159 | GX90S-4-15WW | Sounder Strobe, 24 VDC, 15 cd, UL1971 | 0 | 0.094 | Horn/Strobe
160 | GX90S-4-30WR | Sounder Strobe, 24 VDC, 30 candela, red | 0 | 0.117 | Horn/Strobe
161 | GX90S-4-30WW | Sounder Strobe, 24 VDC, 30 candela, white | 0 | 0.117 | Horn/Strobe
162 | GX90S-4-60WR | Sounder Strobe, 24 VDC, 60 candela, red | 0 | 0.142 | Horn/Strobe
163 | GX90S-4-60WW | Sounder Strobe, 24 VDC, 60 candela, white | 0 | 0.142 | Horn/Strobe
164 | GXS-120177CR | Strobe, 120 Vac, 177 candela, ceiling, red | 0 | 0 | Strobe
165 | GXS-120177CW | Strobe, 120 Vac, 177 candela, ceiling, white | 0 | 0 | Strobe
166 | GXS-120-177WR | Strobe, 120 VAC, UL1971/ADA | 0 | 0 | Strobe
167 | GXS-120-177WW | Strobe, 120 VAC, UL1971/ADA | 0 | 0 | Strobe
168 | GXS-4-110WR | Strobe, 24 VDC, 110 cd, UL1971/ADA | 0 | 0.24 | Strobe
169 | GXS-4-110WW | Strobe, 24 VDC, 110 cd, UL1971/ADA | 0 | 0.24 | Strobe
170 | GXS-4-15/75CR | Strobe, 24 VDC, 15/75 cd | 0 | 0.13 | Strobe
171 | GXS-4-15/75CW | Strobe, 24 VDC, 15/75 cd | 0 | 0.13 | Strobe
172 | GXS-4-15/75WR | Strobe, 24 VDC, 15 (UL1971)75 (UL1638) cd | 0 | 0.105 | Strobe
173 | GXS-4-15/75WRZ | Strobe, 24 Vdc, 15/75 candela, red | 0 | 0.144 | Strobe
174 | GXS-4-15/75WW | Strobe, 24 VDC, 15 (UL1971)75 (UL1638) cd | 0 | 0.105 | Strobe
175 | GXS-4-15/75WWZ | Strobe, 24 Vdc, 15/75 candela, white | 0 | 0.144 | Strobe
176 | GXS-4-15WR | Strobe, 24 VDC, 15 cd, UL1971/ADA | 0 | 0.086 | Strobe
177 | GXS-4-30/75WR | Strobe, 24 VDC, 30/75 cd, UL1971/ADA | 0 | 0.165 | Strobe
178 | GXS-4-30/75WW | Strobe, 24 VDC, 30/75 cd, UL1971/ADA | 0 | 0.173 | Strobe
179 | GXS-4-30WR | Strobe, 24 Vdc, 30 candela, red | 0 | 0.105 | Strobe
180 | GXS-4-30WW | Strobe, 24 Vdc, 30 candela, white | 0 | 0.105 | Strobe
181 | GXS-4-60WR | Strobe, 24 Vdc, 60 candela, red | 0 | 0.13 | Strobe
182 | GXS-4-60WW | Strobe, 24 Vdc, 60 candela, white | 0 | 0.13 | Strobe
183 | H12/24 | Horn Only, 12 or 24 volt, red, wall mount | 0 | 0.024 | Horn
184 | H12/24K | Horn Only, 12 or 24 VDC, weatherproof | 0 | 0.024 | Horn
185 | H12/24W | Horn Only, 12 or 24 volt, white, wall mount | 0 | 0.024 | Horn
186 | HG124R | Horn, 12/24 VDC, 110 dB @ 10ft | 0 | 0.012 | Horn
187 | HG124W | Horn, 12/24 VDC, 110 dB @ 10ft | 0 | 0.012 | Horn
188 | HR | Horn, red | 0 | 0.069 | Horn
189 | HRK | Horn outdoor, red | 0 | 0.069 | Horn
190 | HS24-110WR | Horn Strobe, 110 cd | 0 | 0.146 | Horn/Strobe
191 | HS24-110WW | Horn Strobe, 24 VDC, 110 candela, wall, white | 0 | 0.146 | Horn/Strobe
192 | HS24-15/75WR | Horn Strobe, 24 VDC, 15/75 cd | 0 | 0.092 | Horn/Strobe
193 | HS24-15/75WW | Horn Strobe, 24 VDC, 15/75 cd | 0 | 0.092 | Horn/Strobe
194 | HS24-15WR | Horn Strobe, 24 VDC, 15 cd | 0 | 0.077 | Horn/Strobe
195 | HS24-15WW | Horn Strobe, 24 VDC, 15 cd | 0 | 0.077 | Horn/Strobe
196 | HS24-30WR | Horn Strobe, 24 VDC, 30 cd | 0 | 0.092 | Horn/Strobe
197 | HS24-30WW | Horn Strobe, 24 VDC, 30 candela, wall, white | 0 | 0.092 | Horn/Strobe
198 | HS24-60WR | Horn Strobe, 24 VDC, 60 cd | 0 | 0.125 | Horn/Strobe
199 | HS24-60WW | Horn Strobe, 24 VDC, 60 candela, wall, white | 0 | 0.125 | Horn/Strobe
200 | HW | Horn, white | 0 | 0.069 | Horn
201 | KMS-10-24 | Vibrating Bell, 10", 24 VDC | 0 | 0.03 | Bell
202 | KMS-6-24 | Vibrating Bell, 6", 24 VDC | 0 | 0.03 | Bell
203 | KMS-8-24 | Vibrating Bell, 8", 24 VDC | 0 | 0.03 | Bell
204 | MA-12/24D | Multi-Alert sounder, 12 or 24 VDC | 0 | 0.046 | Horn
205 | MASS24LO | Sounder Strobe, 24 VDC, 1.5 cd | 0 | 0.071 | Horn/Strobe
206 | MASS24LOLA | Sounder Strobe, 24 VDC, 1.5 cd, Spanish | 0 | 0.071 | Horn/Strobe
207 | MASS24M | Sounder Strobe, 24 VDC, 15 cd | 0 | 0.121 | Horn/Strobe
208 | MB-G10-24-R | Motorized Bell, 24 VDC, 10" | 0 | 0.04 | Bell
209 | MB-G6-24-R | Motorized Bell, 24 VDC, 6" | 0 | 0.042 | Bell
210 | MDL | SyncCircuit Module, 12 or 24 VDC | 0 | 0.011 | Sync Module
211 | MDLW | SyncCircuit Module, 12 or 24 VDC | 0 | 0.011 | Sync Module
212 | MR-101/CR | SPDT relay in Red metal enclosure | 0 | 0.015 | Relay Module
213 | MR-104/T | 4 SPDT relays, track mount | 0 | 0.06 | Relay Module
214 | MR-204/T | 4 DPDT relays, track mount | 0 | 0.14 | Relay Module
215 | MTWP-2475W | Weatherproof Audible Strobe - 75 Candela | 0 | 0.149 | Horn/Strobe
216 | NH-12/24-R | Horn, 12/24 VDC, Non-Sync/Sync | 0 | 0.02 | Horn
217 | NS-24110MCW-FR | Horn/Strobe, 24 Vdc, red, selectable, 110 candela | 0 | 0.304 | Horn/Strobe
218 | NS-24110W-FR | Horn Strobe, 24 VDC, 110 cd, Non-Sync/Sync | 0 | 0.34 | Horn/Strobe
219 | NS-241575W-FR | Horn Strobe, 24 VDC, 15/75 cd, Non-Sync/Sync | 0 | 0.12 | Horn/Strobe
220 | NS-2415MCW-FR | Horn/Strobe, 24 Vdc, red, selectable, 15 candela | 0 | 0.08 | Horn/Strobe
221 | NS-2415W-FR | Horn Strobe, 24 VDC, 15 cd, Non-Sync/Sync | 0 | 0.102 | Horn/Strobe
222 | NS-2430MCW-FR | Horn/Strobe, 24 Vdc, red, selectable, 30 candela | 0 | 0.128 | Horn/Strobe
223 | NS-2430W-FR | Horn Strobe, 24 VDC, 30 cd, Non-Sync/Sync | 0 | 0.14 | Horn/Strobe
224 | NS-2475MCW-FR | Horn/Strobe, 24 Vdc, red, selectable, 75 candela | 0 | 0.226 | Horn/Strobe
225 | NS-2475W-FR | Horn Strobe, 24 VDC, 75 cd, Non-Sync/Sync | 0 | 0.23 | Horn/Strobe
226 | NS4-241575W-FR | Horn Strobe, 24 VDC, 15/75 cd, Non-Sync/Sync | 0 | 0.105 | Horn/Strobe
227 | P1224MC110 | Horn Strobe, 24 VDC, 110 cd | 0 | 0.266 | Horn/Strobe
228 | P1224MC110K | Horn Strobe, 24 VDC, 110 cd, Weatherproof | 0 | 0.266 | Horn/Strobe
229 | P1224MC110W | Horn Strobe, 24 VDC, 110 cd | 0 | 0.266 | Horn/Strobe
230 | P1224MC15 | Horn Strobe, 24 VDC, 15 cd | 0 | 0.116 | Horn/Strobe
231 | P1224MC1575 | Horn Strobe, 24 VDC, 15/75 cd | 0 | 0.126 | Horn/Strobe
232 | P1224MC1575F | Horn Strobe, Spanish (Fuego lens) 24 VDC, 15/75 cd | 0 | 0.126 | Horn/Strobe
233 | P1224MC1575K | Horn Strobe, 24 VDC, 15/75 cd, Weatherproof | 0 | 0.126 | Horn/Strobe
234 | P1224MC1575W | Horn Strobe, 24 VDC, 15/75 cd | 0 | 0.126 | Horn/Strobe
235 | P1224MC15K | Horn Strobe, 24 VDC, 15cd, Weatherproof | 0 | 0.116 | Horn/Strobe
236 | P1224MC15W | Horn Strobe, 24 VDC, 15 cd | 0 | 0.116 | Horn/Strobe
237 | P1224MC30 | Horn Strobe, 24 Volt, red, wall mount, 30 candela | 0 | 0.147 | Horn/Strobe
238 | P1224MC30K | Horn Strobe, 24 VDC, 30cd, Weatherproof | 0 | 0.147 | Horn/Strobe
239 | P1224MC30W | Horn Strobe, 24 volt, white wall mount, 30 candela | 0 | 0.147 | Horn/Strobe
240 | P1224MC75 | Horn Strobe, 24 VDC, 75 cd | 0 | 0.217 | Horn/Strobe
241 | P1224MC75K | Horn Strobe, 24 VDC, 75 cd, Weatherproof | 0 | 0.217 | Horn/Strobe
242 | P1224MC75W | Horn Strobe, 24 VDC, 75 cd | 0 | 0.217 | Horn/Strobe
243 | P2R110 | 2-Wire Horn/Strobe 110 cd, red | 0 | 0.221 | Horn/Strobe
244 | P2R115 | 2-Wire Horn/Strobe 115 cd, red | 0 | 0.229 | Horn/Strobe
245 | P2R15 | 2-Wire Horn/Strobe 15 cd, red | 0 | 0.091 | Horn/Strobe
246 | P2R1575 | 2-Wire Horn/Strobe 15/75 cd, red | 0 | 0.1 | Horn/Strobe
247 | P2R30 | 2-Wire Horn/Strobe 30 cd, red | 0 | 0.116 | Horn/Strobe
248 | P2R75 | 2-Wire Horn/Strobe 75 cd, red | 0 | 0.176 | Horn/Strobe
249 | P2R95 | 2-Wire Horn/Strobe 95 cd, red | 0 | 0.201 | Horn/Strobe
250 | P2RH135 | 2-Wire Horn/Strobe 135cd, red | 0 | 0.255 | Horn/Strobe
251 | P2RH150 | 2-Wire Horn/Strobe 150cd, red | 0 | 0.27 | Horn/Strobe
252 | P2RH177 | 2-Wire Horn/Strobe 177cd, red | 0 | 0.303 | Horn/Strobe
253 | P2RH185 | 2-Wire Horn/Strobe 185cd, red | 0 | 0.309 | Horn/Strobe
254 | P2RHK135 | 2-Wire Horn/Strobe outdoor 135cd, red | 0 | 0.255 | Horn/Strobe
255 | P2RHK150 | 2-Wire Horn/Strobe outdoor 150cd, red | 0 | 0.27 | Horn/Strobe
256 | P2RHK177 | 2-Wire Horn/Strobe outdoor 177cd, red | 0 | 0.303 | Horn/Strobe
257 | P2RHK185 | 2-Wire Horn/Strobe outdoor 185cd, red | 0 | 0.309 | Horn/Strobe
258 | P2RK110 | 2-Wire Horn/Strobe outdoor 110 cd, red | 0 | 0.221 | Horn/Strobe
259 | P2RK115 | 2-Wire Horn/Strobe outdoor 115 cd, red | 0 | 0.229 | Horn/Strobe
260 | P2RK15 | 2-Wire Horn/Strobe outdoor 15 cd, red | 0 | 0.091 | Horn/Strobe
261 | P2RK1575 | 2-Wire Horn/Strobe outdoor 15/75 cd, red | 0 | 0.1 | Horn/Strobe
262 | P2RK30 | 2-Wire Horn/Strobe outdoor 30 cd, red | 0 | 0.116 | Horn/Strobe
263 | P2RK75 | 2-Wire Horn/Strobe outdoor 75 cd, red | 0 | 0.176 | Horn/Strobe
264 | P2RK95 | 2-Wire Horn/Strobe outdoor 95 cd, red | 0 | 0.201 | Horn/Strobe
265 | P2W110 | 2-Wire Horn/Strobe 110 cd, white | 0 | 0.221 | Horn/Strobe
266 | P2W115 | 2-Wire Horn/Strobe 115 cd, white | 0 | 0.229 | Horn/Strobe
267 | P2W15 | 2-Wire Horn/Strobe 15 cd, white | 0 | 0.091 | Horn/Strobe
268 | P2W1575 | 2-Wire Horn/Strobe 15/75 cd, white | 0 | 0.1 | Horn/Strobe
269 | P2W30 | 2-Wire Horn/Strobe 30 cd, white | 0 | 0.116 | Horn/Strobe
270 | P2W75 | 2-Wire Horn/Strobe 75 cd, white | 0 | 0.176 | Horn/Strobe
271 | P2W95 | 2-Wire Horn/Strobe 95 cd, white | 0 | 0.201 | Horn/Strobe
272 | P2WH135 | 2-Wire Horn/Strobe 135cd, white | 0 | 0.255 | Horn/Strobe
273 | P2WH150 | 2-Wire Horn/Strobe 150cd, white | 0 | 0.27 | Horn/Strobe
274 | P2WH177 | 2-Wire Horn/Strobe 177cd, white | 0 | 0.303 | Horn/Strobe
275 | P2WH185 | 2-Wire Horn/Strobe 185cd, white | 0 | 0.309 | Horn/Strobe
276 | P4R110 | 4-Wire Horn/Strobe 110 cd, red | 0 | 0.271 | Horn/Strobe
277 | P4R115 | 4-Wire Horn/Strobe 115 cd, red | 0 | 0.279 | Horn/Strobe
278 | P4R15 | 4-Wire Horn/Strobe 15 cd, red | 0 | 0.135 | Horn/Strobe
279 | P4R1575 | 4-Wire Horn/Strobe 15/75 cd, red | 0 | 0.146 | Horn/Strobe
280 | P4R30 | 4-Wire Horn/Strobe 30 cd, red | 0 | 0.163 | Horn/Strobe
281 | P4R75 | 4-Wire Horn/Strobe 75 cd, red | 0 | 0.227 | Horn/Strobe
282 | P4R95 | 4-Wire Horn/Strobe 95 cd, red | 0 | 0.25 | Horn/Strobe
283 | P4RH135 | 4-Wire Horn/Strobe 135 cd, red | 0 | 0.297 | Horn/Strobe
284 | P4RH150 | 4-Wire Horn/Strobe 150 cd, red | 0 | 0.315 | Horn/Strobe
285 | P4RH177 | 4-Wire Horn/Strobe 177 cd, red | 0 | 0.35 | Horn/Strobe
286 | P4RH185 | 4-Wire Horn/Strobe 185 cd, red | 0 | 0.355 | Horn/Strobe
287 | P4RHK135 | 4-Wire Horn/Strobe outdoor 135cd, red | 0 | 0.297 | Horn/Strobe
288 | P4RHK150 | 4-Wire Horn/Strobe outdoor 150cd, red | 0 | 0.315 | Horn/Strobe
289 | P4RHK177 | 4-Wire Horn/Strobe outdoor 177cd, red | 0 | 0.35 | Horn/Strobe
290 | P4RHK185 | 4-Wire Horn/Strobe outdoor 185cd, red | 0 | 0.355 | Horn/Strobe
291 | P4RK110 | 4-Wire Horn/Strobe outdoor 110 cd, red | 0 | 0.271 | Horn/Strobe
292 | P4RK115 | 4-Wire Horn/Strobe outdoor 115 cd, red | 0 | 0.279 | Horn/Strobe
293 | P4RK15 | 4-Wire Horn/Strobe outdoor 15 cd, red | 0 | 0.135 | Horn/Strobe
294 | P4RK1575 | 4-Wire Horn/Strobe outdoor 15/75 cd, red | 0 | 0.146 | Horn/Strobe
295 | P4RK30 | 4-Wire Horn/Strobe outdoor 30 cd, red | 0 | 0.163 | Horn/Strobe
296 | P4RK75 | 4-Wire Horn/Strobe outdoor 75 cd, red | 0 | 0.227 | Horn/Strobe
297 | P4RK95 | 4-Wire Horn/Strobe outdoor 95 cd, red | 0 | 0.25 | Horn/Strobe
298 | P4W110 | 4-Wire Horn/Strobe 110 cd, white | 0 | 0.271 | Horn/Strobe
299 | P4W115 | 4-Wire Horn/Strobe 115 cd, white | 0 | 0.279 | Horn/Strobe
300 | P4W15 | 4-Wire Horn/Strobe 15 cd, white | 0 | 0.135 | Horn/Strobe
301 | P4W1575 | 4-Wire Horn/Strobe 15/75 cd, white | 0 | 0.146 | Horn/Strobe
302 | P4W30 | 4-Wire Horn/Strobe 30 cd, white | 0 | 0.163 | Horn/Strobe
303 | P4W75 | 4-Wire Horn/Strobe 75 cd, white | 0 | 0.227 | Horn/Strobe
304 | P4W95 | 4-Wire Horn/Strobe 95 cd, white | 0 | 0.25 | Horn/Strobe
305 | P4WH135 | 4-Wire Horn/Strobe 135 cd, white | 0 | 0.297 | Horn/Strobe
306 | P4WH150 | 4-Wire Horn/Strobe 150 cd, white | 0 | 0.315 | Horn/Strobe
307 | P4WH177 | 4-Wire Horn/Strobe 177 cd, white | 0 | 0.35 | Horn/Strobe
308 | P4WH185 | 4-Wire Horn/Strobe 185 cd, white | 0 | 0.355 | Horn/Strobe
309 | PA400B | Mini-piezo Horn, 12 or 24 VDC, Beige | 0 | 0.0474 | Horn
310 | PA400R | Mini-piezo Horn, 12 or 24 VDCs, red | 0 | 0.0474 | Horn
311 | PA400W | Mini-piezo Horn, 12 or 24 VDCs, white | 0 | 0.0474 | Horn
312 | PAM-1 | Relay, 10 amp, 24 Vdc - 110 Vac | 0 | 0 | Relay Module
313 | PC24115 | Horn Strobe, ceiling mount, 24 volt, 115 candela, red | 0 | 0.382 | Horn/Strobe
314 | PC24115W | Horn Strobe, ceiling mount, 24 volt, 115 candela, white | 0 | 0.382 | Horn/Strobe
315 | PC2415 | Horn Strobe, ceiling mount, 24 volt, 15 candela, red | 0 | 0.121 | Horn/Strobe
316 | PC241575 | Horn Strobe, ceiling mount, 24 volt, 15/75 candela, red | 0 | 0.135 | Horn/Strobe
317 | PC241575W | Horn Strobe, ceiling mount, 24 volt, 15/75 candela, white | 0 | 0.135 | Horn/Strobe
318 | PC2415W | Horn Strobe, ceiling mount, 24 volt, 15 candela, white | 0 | 0.121 | Horn/Strobe
319 | PC24177 | Horn Strobe, ceiling mount, 24 volt, 177 candela, red | 0 | 0.546 | Horn/Strobe
320 | PC24177W | Horn Strobe, ceiling mount, 24 volt, 177 candela, white | 0 | 0.546 | Horn/Strobe
321 | PC2430 | Horn Strobe, ceiling mount, 24 volt, 30 candela, red | 0 | 0.17 | Horn/Strobe
322 | PC2430W | Horn Strobe, ceiling mount, 24 volt, 30 candela, white | 0 | 0.17 | Horn/Strobe
323 | PC2475 | Horn Strobe, ceiling mount, 24 volt, 75 candela, red | 0 | 0.262 | Horn/Strobe
324 | PC2475W | Horn Strobe, ceiling mount, 24 volt, 75 candela, white | 0 | 0.262 | Horn/Strobe
325 | PC2495 | Horn Strobe, ceiling mount, 24 volt, 95 candela, red | 0 | 0.331 | Horn/Strobe
326 | PC2495W | Horn Strobe, ceiling mount, 24 volt, 95 candela, white | 0 | 0.331 | Horn/Strobe
327 | PC2R110 | 2-Wire Horn/Strobe ceiling 110 cd, red | 0 | 0.221 | Horn/Strobe
328 | PC2R115 | 2-Wire Horn/Strobe ceiling 115 cd, red | 0 | 0.229 | Horn/Strobe
329 | PC2R15 | 2-Wire Horn/Strobe ceiling 15 cd, red | 0 | 0 | Horn/Strobe
330 | PC2R1575 | 2-Wire Horn/Strobe ceiling 15/75 cd, red | 0 | 0.1 | Horn/Strobe
331 | PC2R30 | 2-Wire Horn/Strobe ceiling 30 cd, red | 0 | 0.116 | Horn/Strobe
332 | PC2R75 | 2-Wire Horn/Strobe ceiling 75 cd, red | 0 | 0.176 | Horn/Strobe
333 | PC2R95 | 2-Wire Horn/Strobe ceiling 95 cd, red | 0 | 0.201 | Horn/Strobe
334 | PC2RH135 | 2-Wire Horn/Strobe ceiling 135 cd, red | 0 | 0.255 | Horn/Strobe
335 | PC2RH150 | 2-Wire Horn/Strobe ceiling 150 cd, red | 0 | 0.27 | Horn/Strobe
336 | PC2RH177 | 2-Wire Horn/Strobe ceiling 177 cd, red | 0 | 0.303 | Horn/Strobe
337 | PC2RH185 | 2-Wire Horn/Strobe ceiling 185 cd, red | 0 | 0.309 | Horn/Strobe
338 | PC2RHK135 | 2-Wire Horn/Strobe ceiling/outdoor 135 cd, red | 0 | 0.255 | Horn/Strobe
339 | PC2RHK150 | 2-Wire Horn/Strobe ceiling/outdoor 150 cd, red | 0 | 0.27 | Horn/Strobe
340 | PC2RHK177 | 2-Wire Horn/Strobe ceiling/outdoor 177 cd, red | 0 | 0.303 | Horn/Strobe
341 | PC2RHK185 | 2-Wire Horn/Strobe ceiling/outdoor 185 cd, red | 0 | 0.309 | Horn/Strobe
342 | PC2RK110 | 2-Wire Horn/Strobe ceiling/outdoor 110 cd, red | 0 | 0.221 | Horn/Strobe
343 | PC2RK115 | 2-Wire Horn/Strobe ceiling/outdoor 115 cd, red | 0 | 0.229 | Horn/Strobe
344 | PC2RK15 | 2-Wire Horn/Strobe ceiling/outdoor 15 cd, red | 0 | 0.091 | Horn/Strobe
345 | PC2RK1575 | 2-Wire Horn/Strobe ceiling/outdoor 15/75 cd, red | 0 | 0.1 | Horn/Strobe
346 | PC2RK30 | 2-Wire Horn/Strobe ceiling/outdoor 30 cd, red | 0 | 0.116 | Horn/Strobe
347 | PC2RK75 | 2-Wire Horn/Strobe ceiling/outdoor 75 cd, red | 0 | 0.176 | Horn/Strobe
348 | PC2RK95 | 2-Wire Horn/Strobe ceiling/outdoor 95 cd, red | 0 | 0.201 | Horn/Strobe
349 | PC2W110 | 2-Wire Horn/Strobe ceiling 110 cd, white | 0 | 0.221 | Horn/Strobe
350 | PC2W115 | 2-Wire Horn/Strobe ceiling 115 cd, white | 0 | 0.229 | Horn/Strobe
351 | PC2W15 | 2-Wire Horn/Strobe ceiling 15 cd, white | 0 | 0.091 | Horn/Strobe
352 | PC2W1575 | 2-Wire Horn/Strobe ceiling 15/75 cd, white | 0 | 0.1 | Horn/Strobe
353 | PC2W30 | 2-Wire Horn/Strobe ceiling 30 cd, white | 0 | 0.116 | Horn/Strobe
354 | PC2W75 | 2-Wire Horn/Strobe ceiling 75 cd, white | 0 | 0.176 | Horn/Strobe
355 | PC2W95 | 2-Wire Horn/Strobe ceiling 95 cd, white | 0 | 0.201 | Horn/Strobe
356 | PC2WH135 | 2-Wire Horn/Strobe ceiling 135 cd, white | 0 | 0.255 | Horn/Strobe
357 | PC2WH150 | 2-Wire Horn/Strobe ceiling 150 cd, white | 0 | 0.27 | Horn/Strobe
358 | PC2WH177 | 2-Wire Horn/Strobe ceiling 177 cd, white | 0 | 0.303 | Horn/Strobe
359 | PC2WH185 | 2-Wire Horn/Strobe ceiling 185 cd, white | 0 | 0.309 | Horn/Strobe
360 | PC4R110 | 4-Wire Horn/Strobe ceiling 110 cd, red | 0 | 0.271 | Horn/Strobe
361 | PC4R115 | 4-Wire Horn/Strobe ceiling 115 cd, red | 0 | 0.279 | Horn/Strobe
362 | PC4R15 | 4-Wire Horn/Strobe ceiling 15 cd, red | 0 | 0.135 | Horn/Strobe
363 | PC4R1575 | 4-Wire Horn/Strobe ceiling 15/75 cd, red | 0 | 0.146 | Horn/Strobe
364 | PC4R30 | 4-Wire Horn/Strobe ceiling 30 cd, red | 0 | 0.163 | Horn/Strobe
365 | PC4R75 | 4-Wire Horn/Strobe ceiling 75 cd, red | 0 | 0.227 | Horn/Strobe
366 | PC4R95 | 4-Wire Horn/Strobe ceiling 95 cd, red | 0 | 0.25 | Horn/Strobe
367 | PC4RH135 | 4-Wire Horn/Strobe ceiling 135 cd, red | 0 | 0.297 | Horn/Strobe
368 | PC4RH150 | 4-Wire Horn/Strobe ceiling 150 cd, red | 0 | 0.315 | Horn/Strobe
369 | PC4RH177 | 4-Wire Horn/Strobe ceiling 177 cd, red | 0 | 0.35 | Horn/Strobe
370 | PC4RH185 | 4-Wire Horn/Strobe ceiling 185 cd, red | 0 | 0.355 | Horn/Strobe
371 | PC4RHK135 | 4-Wire Horn/Strobe ceiling/outdoor 135 cd, red | 0 | 0.297 | Horn/Strobe
372 | PC4RHK150 | 4-Wire Horn/Strobe ceiling/outdoor 150 cd, red | 0 | 0.315 | Horn/Strobe
373 | PC4RHK177 | 4-Wire Horn/Strobe ceiling/outdoor 177 cd, red | 0 | 0.35 | Horn/Strobe
374 | PC4RHK185 | 4-Wire Horn/Strobe ceiling/outdoor 185 cd, red | 0 | 0.355 | Horn/Strobe
375 | PC4RK110 | 4-Wire Horn/Strobe ceiling/outdoor 110 cd, red | 0 | 0.271 | Horn/Strobe
376 | PC4RK115 | 4-Wire Horn/Strobe ceiling/outdoor 115 cd, red | 0 | 0.279 | Horn/Strobe
377 | PC4RK15 | 4-Wire Horn/Strobe ceiling/outdoor 15 cd, red | 0 | 0.135 | Horn/Strobe
378 | PC4RK1575 | 4-Wire Horn/Strobe ceiling/outdoor 15/75 cd, red | 0 | 0.146 | Horn/Strobe
379 | PC4RK30 | 4-Wire Horn/Strobe ceiling/outdoor 30 cd, red | 0 | 0.163 | Horn/Strobe
380 | PC4RK75 | 4-Wire Horn/Strobe ceiling/outdoor 75 cd, red | 0 | 0.227 | Horn/Strobe
381 | PC4RK95 | 4-Wire Horn/Strobe ceiling/outdoor 95 cd, red | 0 | 0.25 | Horn/Strobe
382 | PC4W110 | 4-Wire Horn/Strobe ceiling 110 cd, white | 0 | 0.271 | Horn/Strobe
383 | PC4W115 | 4-Wire Horn/Strobe ceiling 115 cd, white | 0 | 0.279 | Horn/Strobe
384 | PC4W15 | 4-Wire Horn/Strobe ceiling 15 cd, white | 0 | 0.135 | Horn/Strobe
385 | PC4W1575 | 4-Wire Horn/Strobe ceiling 15/75 cd, white | 0 | 0.146 | Horn/Strobe
386 | PC4W30 | 4-Wire Horn/Strobe ceiling 30 cd, white | 0 | 0.163 | Horn/Strobe
387 | PC4W75 | 4-Wire Horn/Strobe ceiling 75 cd, white | 0 | 0.227 | Horn/Strobe
388 | PC4W95 | 4-Wire Horn/Strobe ceiling 95 cd, white | 0 | 0.25 | Horn/Strobe
389 | PC4WH135 | 4-Wire Horn/Strobe ceiling 135 cd, white | 0 | 0.297 | Horn/Strobe
390 | PC4WH150 | 4-Wire Horn/Strobe ceiling 150 cd, white | 0 | 0.315 | Horn/Strobe
391 | PC4WH177 | 4-Wire Horn/Strobe ceiling 177 cd, white | 0 | 0.35 | Horn/Strobe
392 | PC4WH185 | 4-Wire Horn/Strobe ceiling 185 cd, white | 0 | 0.355 | Horn/Strobe
393 | PF24 | Exit Point™ Directional Sounder | 0 | 0 | Speaker
394 | PS24LO | Mini-Strobe, 24 VDC | 0 | 0.025 | Strobe
395 | RSS-24100C-FW | Strobe, 24 VDC, 100 cd, Non-Sync/Sync | 0 | 0.375 | Strobe
396 | RSS-24110MCW-FR | Strobe, 24 Vdc, red, selectable, 110 candela | 0 | 0.289 | Strobe
397 | RSS-24110MCW-FW | Strobe, 24 Vdc, white, selectable, 110 candela | 0 | 0.289 | Strobe
398 | RSS-24110W-FR | Strobe, 24 VDC, 110 cd, Non-Sync/Sync | 0 | 0.276 | Strobe
399 | RSS-241575W-FR | Strobe, 24 VDC, 15/75 cd, Non-Sync/Sync | 0 | 0.099 | Strobe
400 | RSS-2415C-FW | Strobe, 24 VDC, 15 cd, Non-Sync/Sync | 0 | 0.105 | Strobe
401 | RSS-2415MCC-FW | CEILING MOUNTED MULTI CANDELA STROBE | 0 | 0.068 | Strobe
402 | RSS-2415MCW-FR | Strobe, 24 Vdc, red, selectable, 15 candela | 0 | 0.07 | Strobe
403 | RSS-2415MCW-FW | Strobe, 24 Vdc, white, selectable, 15 candela | 0 | 0.07 | Strobe
404 | RSS-2415W-FR | Strobe, 24 VDC, 15 cd, Non-Sync/Sync | 0 | 0.072 | Strobe
405 | RSS-24177C-FW | STROBE CEILING MOUNTED | 0 | 0.57 | Strobe
406 | RSS-2430C-FW | Strobe, 24 VDC, 30 cd, Non-Sync/Sync | 0 | 0.158 | Strobe
407 | RSS-2430MCW-FR | Strobe, 24 Vdc, red, selectable, 30 candela | 0 | 0.114 | Strobe
408 | RSS-2430MCW-FW | Strobe, 24 Vdc, white, selectable, 30 candela | 0 | 0.114 | Strobe
409 | RSS-2430W-FR | Strobe, 24 VDC, 30 cd, Non-Sync/Sync | 0 | 0.125 | Strobe
410 | RSS-2475C-FW | Strobe, 24 VDC, 75 cd, Non-Sync/Sync | 0 | 0.33 | Strobe
411 | RSS-2475MCC-FW | Ceiling Mount Multi Candela Strobe at 75cd | 0 | 0.211 | Strobe
412 | RSS-2475MCW-FR | Strobe, 24 Vdc, red, selectable, 75 candela | 0 | 0.22 | Strobe
413 | RSS-2475MCW-FW | Strobe, 24 Vdc, white, selectable, 75 candela | 0 | 0.22 | Strobe
414 | RSS-2475W-FR | Strobe, 24 VDC, 75 cd, Non-Sync/Sync | 0 | 0.215 | Strobe
415 | RTM-8 | Plug-in Relay/Transmitter module | 0 | 0 | Relay Module
416 | RTM-8F | Relay Transmitter Module, 8 Form-C Relays | 0 | 0 | Relay Module
417 | S1224MC110 | Strobe, 24 VDC, 110 cd | 0 | 0.209 | Strobe
418 | S1224MC110K | Strobe, 24 VDC, 110 cd, Weatherproof | 0 | 0.209 | Strobe
419 | S1224MC110W | Strobe, 24 VDC, 110 cd | 0 | 0.209 | Strobe
420 | S1224MC15 | Strobe, 24 VDC, 15 cd | 0 | 0.059 | Strobe
421 | S1224MC1575 | Strobe, 24 VDC, 15/75 cd | 0 | 0.069 | Strobe
422 | S1224MC1575F | Strobe, in Spanish (Fuego) 24 VDC, 15/75 cd | 0 | 0.069 | Strobe
423 | S1224MC1575K | Strobe, 24 VDC, 15/75 cd, Weatherproof | 0 | 0.069 | Strobe
424 | S1224MC1575W | Strobe, 24 VDC, 15/75 cd | 0 | 0.069 | Strobe
425 | S1224MC15K | Strobe, 24 VDC, 15 cd, Weatherproof | 0 | 0.059 | Strobe
426 | S1224MC15W | Strobe, 24 VDC, 15 cd | 0 | 0.059 | Strobe
427 | S1224MC30 | Strobe, 24 Volt, red, 30 candela | 0 | 0.09 | Strobe
428 | S1224MC30K | Strobe, 24 VDC, 30 cd, Weatherproof | 0 | 0.09 | Strobe
429 | S1224MC30W | Strobe, 24 volt, white 30 candela | 0 | 0.09 | Strobe
430 | S1224MC75 | Strobe, 24 VDC, 75 cd | 0 | 0.16 | Strobe
431 | S1224MC75K | Strobe, 24 VDC, 75 cd, Weatherproof | 0 | 0.16 | Strobe
432 | S1224MC75W | Strobe, 24 VDC, 75 cd | 0 | 0.16 | Strobe
433 | SC24115 | Strobe, Ceiling mount, 24 volt, 115 candela, red | 0 | 0.325 | Strobe
434 | SC24115W | Strobe, Ceiling mount, 24 volt, 115 candela, white | 0 | 0.325 | Strobe
435 | SC2415 | Strobe, Ceiling Mount, 24 volt, red, 15 candela | 0 | 0.064 | Strobe
436 | SC241575 | Strobe, Ceiling Mount, 24 volt, red, 15/75 candela | 0 | 0.078 | Strobe
437 | SC241575W | Strobe, Ceiling Mount, 24 volt, white, 15/75 candela | 0 | 0.078 | Strobe
438 | SC2415W | Strobe, Ceiling Mount, 24 volt, white, 15 candela | 0 | 0.064 | Strobe
439 | SC24177 | Strobe, Ceiling Mount, 24 volt, red, 177 candela | 0 | 0.489 | Strobe
440 | SC24177W | Strobe, Ceiling Mount, 24 volt, white, 177 candela | 0 | 0.489 | Strobe
441 | SC2430 | Strobe, Ceiling Mount, 24 volt, red, 30 candela | 0 | 0.113 | Strobe
442 | SC2430W | Strobe, Ceiling Mount, 24 volt, white, 30 candela | 0 | 0.113 | Strobe
443 | SC2475 | Strobe, Ceiling Mount, 24 volt, red, 75 candela | 0 | 0.205 | Strobe
444 | SC2475W | Strobe, Ceiling Mount, 24 volt, white, 75 candela | 0 | 0.205 | Strobe
445 | SC2495 | Strobe, Ceiling Mount, 24 volt, red, 95 candela | 0 | 0.274 | Strobe
446 | SC2495W | Strobe, Ceiling Mount, 24 volt, white, 95 candela | 0 | 0.274 | Strobe
447 | SCR110 | Ceiling Strobe 110 cd, red | 0 | 0.202 | Strobe
448 | SCR115 | Ceiling Strobe 115 cd, red | 0 | 0.21 | Strobe
449 | SCR15 | Ceiling Strobe 15 cd, red | 0 | 0.066 | Strobe
450 | SCR1575 | Ceiling Strobe 15/75 cd, red | 0 | 0.077 | Strobe
451 | SCR30 | Ceiling Strobe 30 cd, red | 0 | 0.094 | Strobe
452 | SCR75 | Ceiling Strobe 75 cd, red | 0 | 0.158 | Strobe
453 | SCR95 | Ceiling Strobe 95 cd, red | 0 | 0.181 | Strobe
454 | SCRH135 | Ceiling Strobe 135 cd, red | 0 | 0.228 | Strobe
455 | SCRH150 | Ceiling Strobe 150 cd, red | 0 | 0.246 | Strobe
456 | SCRH177 | Ceiling Strobe 177 cd, red | 0 | 0.281 | Strobe
457 | SCRH185 | Ceiling Strobe 185 cd, red | 0 | 0.286 | Strobe
458 | SCRHK135 | Ceiling Strobe outdoor 135 cd, red | 0 | 0.228 | Strobe
459 | SCRHK150 | Ceiling Strobe outdoor 150 cd, red | 0 | 0.246 | Strobe
460 | SCRHK177 | Ceiling Strobe outdoor 177 cd, red | 0 | 0.281 | Strobe
461 | SCRHK185 | Ceiling Strobe outdoor 185 cd, red | 0 | 0.286 | Strobe
462 | SCRK110 | Ceiling Strobe outdoor 110 cd, red | 0 | 0.202 | Strobe
463 | SCRK115 | Ceiling Strobe outdoor 115 cd, red | 0 | 0.21 | Strobe
464 | SCRK15 | Ceiling Strobe outdoor 15 cd, red | 0 | 0.066 | Strobe
465 | SCRK1575 | Ceiling Strobe outdoor 15/75 cd, red | 0 | 0.077 | Strobe
466 | SCRK30 | Ceiling Strobe outdoor 30 cd, red | 0 | 0.094 | Strobe
467 | SCRK75 | Ceiling Strobe outdoor 75 cd, red | 0 | 0.158 | Strobe
468 | SCRK95 | Ceiling Strobe outdoor 95 cd, red | 0 | 0.181 | Strobe
469 | SCW110 | Ceiling Strobe 110 cd, white | 0 | 0.202 | Strobe
470 | SCW115 | Ceiling Strobe 115 cd, white | 0 | 0.21 | Strobe
471 | SCW15 | Ceiling Strobe 15 cd, white | 0 | 0.066 | Strobe
472 | SCW1575 | Ceiling Strobe 15/75 cd, white | 0 | 0.077 | Strobe
473 | SCW30 | Ceiling Strobe 30 cd, white | 0 | 0.094 | Strobe
474 | SCW75 | Ceiling Strobe 75 cd, white | 0 | 0.158 | Strobe
475 | SCW95 | Ceiling Strobe 95 cd, white | 0 | 0.181 | Strobe
476 | SCWH135 | Ceiling Strobe 135 cd, white | 0 | 0.228 | Strobe
477 | SCWH150 | Ceiling Strobe 150 cd, white | 0 | 0.246 | Strobe
478 | SCWH177 | Ceiling Strobe 177 cd, white | 0 | 0.281 | Strobe
479 | SCWH185 | Ceiling Strobe 185 cd, white | 0 | 0.286 | Strobe
480 | SHG24-110WW | Horn Strobe, 24 VDC, white, 110 cd, UL1971/ADA | 0 | 0.252 | Horn/Strobe
481 | SHG24-15/75CR | Horn Strobe, 24 VDC, 15/75 cd | 0 | 0.142 | Horn/Strobe
482 | SHG24-15/75CW | Horn Strobe, 24 VDC, 15/75 cd | 0 | 0.142 | Horn/Strobe
483 | SHG24-15/75WR | Horn Strobe, 24 VDC, 15 (UL1971)/75 (UL1638) cd | 0 | 0.117 | Horn/Strobe
484 | SHG24-15/75WRZ | Horn Strobe, 24 VDC, 15/75 cd | 0 | 0.156 | Horn/Strobe
485 | SHG24-15/75WW | Horn Strobe, 24 VDC, 15 (UL1971)/75 (UL1638) cd | 0 | 0.117 | Horn/Strobe
486 | SHG24-15/75WWZ | Horn Strobe, 24 VDC, 15/75 cd | 0 | 0.156 | Horn/Strobe
487 | SHG24-15WR | Horn Strobe, 24 VDC, 15 cd, UL1971/ADA | 0 | 0.098 | Horn/Strobe
488 | SHG24-15WW | Horn Strobe, 24 VDC, 15 cd, UL1971/ADA | 0 | 0.098 | Horn/Strobe
489 | SHG24-30/75WR | Horn Strobe, 24 VDC, 30/75 cd, UL1971/ADA | 0 | 0.177 | Horn/Strobe
490 | SHG24-30/75WW | Horn Strobe, 24 VDC, 30/75 cd, UL1971/ADA | 0 | 0.177 | Horn/Strobe
491 | SHG24-30WR | Horn Strobe, 24 VDC, 30 cd, UL1971/ADA | 0 | 0.117 | Horn/Strobe
492 | SHG24-30WW | Horn Strobe, 24 Vdc, white, 30 candela | 0 | 0.117 | Horn/Strobe
493 | SHG24-60WR | Horn Strobe, 24 VDC, 60 cd, UL1971/ADA | 0 | 0.142 | Horn/Strobe
494 | SHG24-60WW | Horn Strobe, 24 Vdc, white, 60 candela | 0 | 0.142 | Horn/Strobe
495 | SM-12/24-R | Sync Module, single circuit Class B, 12 or 24 VDC | 0 | 0.07 | Sync Module
496 | SM24-10 | Bell, 24 VDC, 10" Gong Diameter | 0 | 0.053 | Bell
497 | SM24-6 | Bell, 24 VDC, 6" Gong Diameter | 0 | 0.053 | Bell
498 | SM24-8 | Bell, 24 VDC, 8" Gong Diameter | 0 | 0.053 | Bell
499 | SP200W | Speaker, round, white, 25 or 70.7 vrms | 0 | 0 | Speaker
500 | SP201R | Speaker, square, red, 25 or 70.7 vrms | 0 | 0 | Speaker
501 | SP201W | Speaker, square, white 25 or 70.7 vrms | 0 | 0 | Speaker
502 | SP2C24115 | Speaker Strobe, 24 volt, 115 candela, white, Ceiling | 0 | 0.325 | Speaker/Strobe
503 | SP2C2415 | Speaker Strobe, 24 volt,15 candela, white, Ceiling | 0 | 0.064 | Speaker/Strobe
504 | SP2C241575 | Speaker Strobe, 24 volt,15/75 candela, white, Ceiling | 0 | 0.078 | Speaker/Strobe
505 | SP2C24177 | Speaker Strobe, 24 volt, 177 candela, white, Ceiling | 0 | 0.489 | Speaker/Strobe
506 | SP2C2430 | Speaker Strobe, 24 volt, 30 candela, white, Ceiling | 0 | 0.113 | Speaker/Strobe
507 | SP2C2475 | Speaker Strobe, 24 volt, 75 candela, white, Ceiling | 0 | 0.205 | Speaker/Strobe
508 | SP2C2495 | Speaker Strobe, 24 volt, 95 candela, white, Ceiling | 0 | 0.274 | Speaker/Strobe
509 | SP2R1224MC110 | Spkr/Strobe, 24 vdc, 110C, Red, Wall | 0 | 0.209 | Speaker/Strobe
510 | SP2R1224MC15 | Spkr/Strobe, 24 vdc, 15C, Red, Wall | 0 | 0.059 | Speaker/Strobe
511 | SP2R1224MC1575 | Spkr/Strobe, 24 vdc, 15/75C, Red, Wall | 0 | 0.069 | Speaker/Strobe
512 | SP2R1224MC30 | Spkr/Strobe, 24 vdc, 30C, Red, Wall | 0 | 0.09 | Speaker/Strobe
513 | SP2R1224MC75 | Spkr/Strobe, 24 vdc, 75C, Red, Wall | 0 | 0.16 | Speaker/Strobe
514 | SP2W1224MC110 | Spkr/Strobe, 24 vdc, 110C, WH, Wall | 0 | 0.209 | Speaker/Strobe
515 | SP2W1224MC15 | Spkr/Strobe, 24 vdc, 15C, Wh, Wall | 0 | 0.059 | Speaker/Strobe
516 | SP2W1224MC1575 | Spkr/Strobe, 24 vdc, 15/75C, Wh, Wall | 0 | 0.069 | Speaker/Strobe
517 | SP2W1224MC30 | Speaker Strobe, 24 volt, 30 candela, white, Wall | 0 | 0.09 | Speaker/Strobe
518 | SP2W1224MC75 | Spkr/Strobe, 24 vdc, 75C, Wh, Wall | 0 | 0.16 | Speaker/Strobe
519 | SPKE4-110WR | Speaker Strobe, 24 VDC, UL1971/ADA, 110 cd | 0 | 0.24 | Speaker/Strobe
520 | SPKE4-110WW | Speaker Strobe, 24 VDC, UL1971/ADA, 110 cd | 0 | 0.24 | Speaker/Strobe
521 | SPKE4-15/75CR | Speaker Strobe, 24 VDC, 15/75 cd | 0 | 0.13 | Speaker/Strobe
522 | SPKE4-15/75CW | Speaker Strobe, 24 VDC, 15/75 cd | 0 | 0.13 | Speaker/Strobe
523 | SPKE4-15/75WR | Speaker Strobe, 24 VDC, 15/75 cd | 0 | 0.108 | Speaker/Strobe
524 | SPKE4-15/75WRZ | Speaker Strobe, 24 VDC, 15/75, 4" square | 0 | 0.144 | Speaker/Strobe
525 | SPKE4-15/75WW | Speaker Strobe, 24 VDC, 15/75 cd | 0 | 0.105 | Speaker/Strobe
526 | SPKE4-15/75WWZ | Speaker Strobe, 24 VDC, 15/75 cd, 4" square | 0 | 0.144 | Speaker/Strobe
527 | SPKE4-15WR | Speaker Strobe, 24 VDC, UL1971/ADA, 15 cd | 0 | 0.086 | Speaker/Strobe
528 | SPKE4-15WW | Speaker Strobe, 24 VDC, UL1971/ADA, 15 cd | 0 | 0.086 | Speaker/Strobe
529 | SPKE4-30/75WR | Speaker Strobe, 4" square 24 VDC, 3075 cd | 0 | 0.165 | Speaker/Strobe
530 | SPKE4-30/75WW | Speaker Strobe, 4" square 24 VDC, 3075 cd | 0 | 0.165 | Speaker/Strobe
531 | SPKE4-30WR | Speaker Strobe, 24 Vdc, 30 candela, wall mount, red | 0 | 0.105 | Speaker/Strobe
532 | SPKE4-30WW | Speaker Strobe, 24 Vdc, 30 candela, wall mount, white | 0 | 0.105 | Speaker/Strobe
533 | SPKE4-60WR | Speaker Strobe, 24 Vdc, 60 candela, wall mount, red | 0 | 0.13 | Speaker/Strobe
534 | SPKE4-60WW | Speaker Strobe, 24 Vdc, 60 candela, wall mount, white | 0 | 0.13 | Speaker/Strobe
535 | SPKE4R | Speaker, 4", 25 or 70.7 Vrms, 1/4 to 2 Watt Taps | 0 | 0 | Speaker
536 | SPKE4W | Speaker, 4", 1/4 to 2 Watt Taps | 0 | 0 | Speaker
537 | SPKE8-110WR | Speaker Strobe, 8" round, 24 VDC, 110 cd | 0 | 0.24 | Speaker/Strobe
538 | SPKE8-110WW | Speaker Strobe, 8" round, 24 VDC, 110 cd | 0 | 0.24 | Speaker/Strobe
539 | SPKE8-15/75CR | Speaker Strobe, 24 VDC, 15/75 cd | 0 | 0.13 | Speaker/Strobe
540 | SPKE8-15/75CW | Speaker Strobe, 24 VDC, 15/75 cd | 0 | 0.13 | Speaker/Strobe
541 | SPKE8-15/75WR | Speaker Strobe, 8" round, 24 VDC, 15/75 cd | 0 | 0.105 | Speaker/Strobe
542 | SPKE8-15/75WRZ | Speaker Strobe, 24 VDC, 15/75 cd, 8" round | 0 | 0.144 | Speaker/Strobe
543 | SPKE8-15/75WW | Speaker Strobe, 8" round, 24 VDC, 15/75 cd | 0 | 0.105 | Speaker/Strobe
544 | SPKE8-15/75WWZ | Speaker Strobe, 24 VDC, 15/75 cd, 8" round | 0 | 0.144 | Speaker/Strobe
545 | SPKE8-15WR | Speaker Strobe, 8" round, 24 VDC, 15 cd | 0 | 0.086 | Speaker/Strobe
546 | SPKE8-15WW | Speaker Strobe, 8" round, 24 VDC, 15 cd | 0 | 0.086 | Speaker/Strobe
547 | SPKE8-30/75WR | Speaker Strobe, red, 8" round, 24 VDC, 3075 cd | 0 | 0.165 | Speaker/Strobe
548 | SPKE8-30/75WW | Speaker Strobe, white, 8" round, 24 VDC, 3075 cd | 0 | 0.165 | Speaker/Strobe
549 | SPKE8-30WR | Speaker strobe, red, 8 inch round, 24 Vdc, 30 candela | 0 | 0.105 | Speaker/Strobe
550 | SPKE8-30WW | Speaker strobe, white, 8 inch round, 24 Vdc, 30 candela | 0 | 0.105 | Speaker/Strobe
551 | SPKE8-60WR | Speaker strobe, red, 8 inch round, 24 Vdc, 60 candela | 0 | 0.13 | Speaker/Strobe
552 | SPKE8-60WW | Speaker strobe, white, 8 inch round, 24 Vdc, 60 candela | 0 | 0.13 | Speaker/Strobe
553 | SPKE8R | Speaker, 8" round, red, 1/4 to 2 Watt Taps | 0 | 0 | Speaker
554 | SPKE8W | Speaker, 8" round, white 1/4 to 2 Watt Taps | 0 | 0 | Speaker
555 | SR110 | Strobe 110 cd, red | 0 | 0.202 | Strobe
556 | SR115 | Strobe 115 cd, red | 0 | 0.21 | Strobe
557 | SR15 | Strobe 15 cd, red | 0 | 0.066 | Strobe
558 | SR1575 | Strobe 15/75 cd, red | 0 | 0.077 | Strobe
559 | SR30 | Strobe 30 cd, red | 0 | 0.094 | Strobe
560 | SR75 | Strobe 75 cd, red | 0 | 0.158 | Strobe
561 | SR95 | Strobe 95 cd, red | 0 | 0.181 | Strobe
562 | SRH135 | Strobe 135 cd, red | 0 | 0.228 | Strobe
563 | SRH150 | Strobe 150 cd, red | 0 | 0.246 | Strobe
564 | SRH177 | Strobe 177 cd, red | 0 | 0.281 | Strobe
565 | SRH185 | Strobe 185 cd, red | 0 | 0.286 | Strobe
566 | SRHK135 | Strobe outdoor 135 cd, red | 0 | 0.228 | Strobe
567 | SRHK150 | Strobe outdoor 150 cd, red | 0 | 0.246 | Strobe
568 | SRHK177 | Strobe outdoor 177 cd, red | 0 | 0.281 | Strobe
569 | SRHK185 | Strobe outdoor 185 cd, red | 0 | 0.286 | Strobe
570 | SRK110 | Strobe outdoor 110 cd, red | 0 | 0.202 | Strobe
571 | SRK115 | Strobe outdoor 115 cd, red | 0 | 0.21 | Strobe
572 | SRK15 | Strobe outdoor 15 cd, red | 0 | 0.066 | Strobe
573 | SRK1575 | Strobe outdoor 15/75 cd, red | 0 | 0.077 | Strobe
574 | SRK30 | Strobe outdoor 30 cd, red | 0 | 0.094 | Strobe
575 | SRK75 | Strobe outdoor 75 cd, red | 0 | 0.158 | Strobe
576 | SRK95 | Strobe outdoor 95 cd, red | 0 | 0.181 | Strobe
577 | SS24LO | Strobe, 24 VDC, 1.5 cd, SSD | 0 | 0.025 | Strobe
578 | SS24M | Strobe, 24 VDC, 15 cd, SSD | 0 | 0.075 | Strobe
579 | SSM24-10 | Bell, 24 VDC, 10" Gong Diameter | 0 | 0.053 | Bell
580 | SSM24-6 | Bell, 24 VDC, 6" Gong Diameter | 0 | 0.053 | Bell
581 | SSM24-8 | Bell, 24 VDC, 8" Gong Diameter | 0 | 0.053 | Bell
582 | SSV120-10 | Bell, 120 VAC, 10" Gong Diameter | 0 | 0.053 | Bell
583 | SSV120-6 | Bell, 120 VAC, 6" Gong Diameter | 0 | 0.053 | Bell
584 | SSV120-8 | Bell, 120 VAC, 8" Gong Diameter | 0 | 0.053 | Bell
585 | ST24-110WR | Strobe, 24VDC, 110 cd | 0 | 0.121 | Strobe
586 | ST24-110WW | Strobe, 24 Vdc, 110 candela, wall, white | 0 | 0.121 | Strobe
587 | ST24-15/75WR | Strobe, 24VDC, 15/75 cd | 0 | 0.067 | Strobe
588 | ST24-15/75WW | Strobe, 24VDC, 15/75 cd | 0 | 0.067 | Strobe
589 | ST24-15WR | Strobe, 24VDC, 15 cd | 0 | 0.052 | Strobe
590 | ST24-15WW | Strobe, 24VDC, 15 cd | 0 | 0.052 | Strobe
591 | ST24-30WR | Strobe, 24VDC, 30 cd | 0 | 0.067 | Strobe
592 | ST24-30WW | Strobe, 24 Vdc, 30 candela, wall, white | 0 | 0.067 | Strobe
593 | ST24-60WR | Strobe, 24VDC, 60 cd | 0 | 0.1 | Strobe
594 | ST24-60WW | Strobe, 24 Vdc, 60 candela, wall, white | 0 | 0.1 | Strobe
595 | ST24-75WR | Strobe, 24 Vdc, 75 candela, wall, red | 0 | 0.103 | Strobe
596 | ST24-75WW | Strobe, 24 Vdc, 75 candela, wall, white | 0 | 0.103 | Strobe
597 | STH-15S | Loud Speaker, 1 to 15 watt, 25/70 Vrms | 0 | 0 | Speaker
598 | STH-15SR | Loud Speaker, 1 to 15 watt, 25/70 Vrms | 0 | 0 | Speaker
599 | SV120-10 | Bell, 120 VAC, 10" Gong Diameter | 0 | 0.053 | Bell
600 | SV120-6 | Bell, 120 VAC, 6" Gong Diameter | 0 | 0.053 | Bell
601 | SV120-8 | Bell, 120 VAC, 8" Gong Diameter | 0 | 0.053 | Bell
602 | SW110 | Strobe 110 cd, white | 0 | 0.202 | Strobe
603 | SW115 | Strobe 115 cd, white | 0 | 0.21 | Strobe
604 | SW15 | Strobe 15 cd, white | 0 | 0.066 | Strobe
605 | SW1575 | Strobe 15/75 cd, white | 0 | 0.077 | Strobe
606 | SW30 | Strobe 30 cd, white | 0 | 0.094 | Strobe
607 | SW75 | Strobe 75 cd, white | 0 | 0.158 | Strobe
608 | SW95 | Strobe 95 cd, white | 0 | 0.181 | Strobe
609 | SWH135 | Strobe 135 cd, white | 0 | 0.228 | Strobe
610 | SWH150 | Strobe 150 cd, white | 0 | 0.246 | Strobe
611 | SWH177 | Strobe 177 cd, white | 0 | 0.281 | Strobe
612 | SWH185 | Strobe 185 cd, white | 0 | 0.286 | Strobe
613 | V-400B | Speaker, 4" square, 25 or 70.7 Vrms | 0 | 0 | Speaker
614 | V-400R | Speaker, 4" square, 25 or 70.7 Vrms | 0 | 0 | Speaker
615 | V-400W | Speaker, 4" square, 24 or 70.7 Vrms | 0 | 0 | Speaker
616 | VB10-120 | Vibrating Bell, 10", 120 VAC | 0 | 0 | Bell
617 | VB10-24 | Vibrating Bell, 10", 24 VAC | 0 | 0.18 | Bell
618 | VB6-120 | Vibrating Bell, 6", 120 VAC | 0 | 0 | Bell
619 | VB6-24 | Vibrating Bell, 6", 24 VAC | 0 | 0.18 | Bell
620 | VB8-120 | Vibrating Bell, 8", 120 VAC | 0 | 0 | Bell
621 | VB8-24 | Vibrating Bell, 8", 24 VAC | 0 | 0.18 | Bell
622 | WGMS24-75-CR | Horn Strobe, 24 VDC, 75 cd, weatherproof | 0 | 0.158 | Horn/Strobe
623 | WGMS24-75-WR | Horn Strobe, 24 VDC, 75 cd, weatherproof | 0 | 0.158 | Horn/Strobe
624 | ZMS4 | Sync Module, GXS, GX90S, SHG, GMS, SPKE4/SPKE8 | 0 | 0.019 | Sync Module
Note on E6: Current (in amps) drawn by a component from the control panel power supply while AC power is ON and the system is NOT in alarm.
Note on F6: FILTERED current (in amps) drawn by a component control panel power supply while AC power is ON and the system is in alarm.