## 411UDAC
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns in the yellow cells to enter values.
411UDAC Battery Calculation
Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[11 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) |  |  |  |  | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total | 20 Minutes | 0.334 | 72 Hours | 72
1. System | [10 empty] | 25 Minutes | 0.417 | 90 Hours | 90
Main Circuit Board | 1 | x | 0.125 | = | 0.125 | 1 | x | 0.18 | = | 0.18 | 30 Minutes | 0.5
2. Notification Appliances
NAC Device 1 | 0 | x | 0 | = |  | 0 | x | 0 | =
NAC Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
NAC Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
NAC Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
NAC Device 5 | 0 | x | 0 | = |  | 0 | x | 0 | =
NAC Device 6 | 0 | x | 0 | = |  | 0 | x | 0 | =
NAC Device 7 | 0 | x | 0 | = |  | 0 | x | 0 | =
NAC Device 8 | 0 | x | 0 | = |  | 0 | x | 0 | =
NAC Standby Draw |  |  |  |  | 0 | NAC Alarm Draw |  |  |  | 0
3. Resettable Power
4-Wire Detectors | 0 | x | 0 | = |  | 0 | x | 0 | =
Additional Draw 12VDC Resettable | 0 | x | 0 | = |  | 0 | x | 0 | =
Resettable Standby Draw |  |  |  |  | 0 | Resettable Alarm Draw |  |  |  | 0
4. Additional Devices
EOLR-1 | 0 | x | 0.02 | = |  | 0 | x | 0.02 | =
Auxiliary Device 1 | 0 | x | 0 | = |  | 0 | x | 0 | =
Auxiliary Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
Auxiliary Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
Auxiliary Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
Auxiliary Device 5 | 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0.125 | Total Alarm Load |  |  |  | 0.18
411UDAC Battery Calculation
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.125 |  |  | x | 24 |  | = | 3
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 0.18 |  |  | x | 0.084 |  | = | 0.01512
Total Current Load | [9 empty] | 3.0151
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 3.6181
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Battery
Battery Check
The batteries can be charged by the 411UDAC Charger.
The batteries can be housed in the 411UDAC Cabinet.
Current Draw Check
NAC#1 current is within the limitations of the circuit.
411UDAC Control Panel:
The output current is within the panel's limitations.
Note on B20: Total NAC Draw cannot exceed 1.0 Amps.
Note on B24: Total Resettable Draw cannot exceed 0.200 Amps.
Note on H20: Total NAC Draw cannot exceed 1.0 Amps.
Note on H24: Total Resettable Draw cannot exceed 0.200 Amps.
Note on H40: Select Standby Time in Hours from the dropdown list.
Note on H43: Select the Alarm Time in minutes from the dropdown list.
Note on H46: Select the Derating Factor from the dropdown list.