## ES-50X
Note 1: You are fully responsible for verifying these calculations. | [10 empty] | Version 10.30.2019
Note 2: Use the dropdowns in the yellow cells to enter values.
ES-50X Battery Calculation
Secondary Power Source Requirements | [11 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[12 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) | [5 empty] | 15 Minutes | 0.25 | 60 Hours | 60
Device | Qty |  | Current Draw |  | Total | Qty |  | Current Draw |  | Total |  | 20 Minutes | 0.334 | 72 Hours | 72
Main Circuit Board | 1 | x | 0.141 | = | 0.141 | 1 | x | 0.257 | = | 0.257 |  | 25 Minutes | 0.417 | 90 Hours | 90
IPOTS-COM Communicator | 1 | x | 0.04 | = | 0.04 | 1 | x | 0.041 | = | 0.041 |  | 30 Minutes | 0.5
4XTMF | 0 | x | 0.005 | = |  | 0 | x | 0.011 | = |  |  | 60 Minutes | 1
EOLR-1 | 0 | x | 0.02 | = |  | 0 | x | 0.02 | = |  |  | 90 Minutes | 1.5
CELL-MOD-FL / CELL-CAB | 1 | x | 0.055 | = | 0.055 | 1 | x | 0.1 | = | 0.1 |  | 180 Minutes | 3
ANN-BUS Devices
ANN-SEC Card | 0 | x | 0.003 | = |  | 0 | x | 0.003 | =
ANN-80(-W) | 1 | x | 0.015 | = | 0.015 | 1 | x | 0.04 | = | 0.04
ANN-100 | 0 | x | 0.02 | = |  | 0 | x | 0.025 | =
ANN-(R)LED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
ANN-RLY | 0 | x | 0.015 | = |  | 0 | x | 0.075 | =
ANN-I/O | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
ANN-I/O LED | 0 | x | 0 | = |  | 0 | x | 0.01 | =
ANN-S/PG | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
Addressable Devices
BEAM355 | 0 | x | 0.002 | =
BEAM355S | 0 | x | 0.002 | =
CP355 | 0 | x | 0.0003 | =
SD365CO | 0 | x | 0.002
SD355CO | 0 | x | 0.0003 | =
SD355 | 0 | x | 0.0003 | =
SD365 | 8 | x | 0.0002 | = | 0.0016
SD355T | 0 | x | 0.0003 | =
SD365T | 0 | x | 0.0002 | =
H355 | 0 | x | 0.0003 | =
H365 | 5 | x | 0.0002 | = | 0.001
H355HT | 0 | x | 0.0003 | =
H365HT | 0 | x | 0.0002 | =
H350R | 0 | x | 0.0003 | =
H355R | 0 | x | 0.0003 | =
H365R | 0 | x | 0.0002 | =
D350RPL | 0 | x | 0.0003 | =
D355PL | 0 | x | 0.0003 | =
MMF-300 | 0 | x | 0.000375 | =
MMF-300-10 | 0 | x | 0.0035 | =
MDF-300 | 0 | x | 0.00075 | =
MMF-301 | 3 | x | 0.00035 | = | 0.00105
MMF-302 | 0 | x | 0.00027 | =
MMF-302-6 | 0 | x | 0.002 | =
BG-12LX | 4 | x | 0.000375 | = | 0.0015
CMF-300 | 0 | x | 0.00039 | =
CMF-300-6 | 0 | x | 0.00225 | =
CRF-300 | 1 | x | 0.000255 | = | 0.000255
CRF-300-6 | 0 | x | 0.00145 | =
CDRM-300 | 0 | x | 0.0013 | =
I300 | 0 | x | 0.0004 | =
ISO-6 | 0 | x | 0.0027 | =
B501BH-2 | 0 | x | 0.001 | =
B501BHT-2 | 0 | x | 0.001 | =
B224RB | 0 | x | 0.0005 | =
B224BI | 0 | x | 0.00045 | =
W-GATE | 0 | x | 0.024 | =
| Maximum alarm draw for all Addressable devices ---------------> | [8 empty] | 0.2
Resettable Power
4-Wire Smoke Detectors | 0 | x | 0 | = |  | 0 | x | 0 | =
SWIFT Wireless
W-GATE | 0 | x | 0.04 | = |  | 0 | x | 0.04 | =
Auxiliary Power
CMF-300 (Aux. Power) | 0 | x | 0.0017 | = |  | 0 | x | 0.007 | =
CMF-300-6 (Aux. Power) | 0 | x | 0.008 | = |  | 0 | x | 0.02 | =
MMF-302 (Aux. Power) | 0 | x | 0.012 | = |  | 0 | x | 0.09 | =
MMF-302-6 (Aux. Power) | 0 | x | 0.05 | = |  | 0 | x | 0.27 | =
B200SR (Aux. Power) | 0 | x | 0.0005 | = |  | 0 | x | 0.035 | =
B200SR-LF (Aux. Power) | 0 | x | 0.001 | = |  | 0 | x | 0.125 | =
Miscellaneous Devices
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Output Circuits
NAC/Output #1 |  |  | 0 | = |  |  |  | 0.557 | = | 0.557
NAC/Output #2 |  |  | 0 | = |  |  |  | 0.639 | = | 0.639
FCPS (remote Sync) | 0 | x | 0 | = |  | 0 | x | 0.0217 | =
Total Standby Load |  |  |  |  | 0.2564 | Total Alarm Load |  |  |  | 1.834
ES-50X Battery Calculation
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Total Standby Current |  |  | 0.2564 |  |  | x | 24 |  | = | 6.1537
Required Alarm Time in Minutes
5 Minutes
Total Alarm Load |  |  | 1.834 |  |  | x | 0.084 |  | = | 0.15406
Total Current Load | [9 empty] | 6.3078
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 7.5693
Recommended Batteries: | [5 empty] | BAT-12120 - 12AH Batteries
Battery Check
The batteries can be charged by the ES-50X Charger.
The batteries can be housed in the ES-50X Cabinet.
Current Draw Check
NAC#1 current is within the limitations of the circuit.
NAC#2 current is within the limitations of the circuit.
ES-50X current draw:
The required output current is within the panel's limitations
ES-50X Circuit Detail
NAC/Output #1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
SRL 15 | 3 | x | 0 | = | 0 | 3 | x | 0.043 | = | 0.129
P2RL 15 | 1 | x | 0 | = | 0 | 1 | x | 0.054 | = | 0.054
P2RL 110 | 1 | x | 0 | = | 0 | 1 | x | 0.162 | = | 0.162
P2RK 110 | 1 | x | 0 | = | 0 | 1 | x | 0.212 | = | 0.212
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0.557
NAC/Output #2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
SRL 15 | 2 | x | 0 | = | 0 | 2 | x | 0.043 | = | 0.086
P2RL 15 | 2 | x | 0 | = | 0 | 2 | x | 0.054 | = | 0.108
P2RL 110 | 1 | x | 0 | = | 0 | 1 | x | 0.162 | = | 0.162
PC2RK 30 | 1 | x | 0 | = | 0 | 1 | x | 0.107 | = | 0.107
PC2RK 75 | 1 | x | 0 | = | 0 | 1 | x | 0.176 | = | 0.176
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0.639
Note on B14: NOTE: There cannot be both ANN-BUS Devices and ACS Annunciators connected to the Control Panel. Choose ANN-BUS or ACS NOT both.
Note on B60: Only enter quantities for W-GATE that are being powered on the SLC.
Note on E63: Refer to the Device Compatibility Document for standby current.
Note on B65: Only enter quantities for W-GATE that are being powered by a Non-Resettable circuit.
Note on B66: Only add those devices that are drawing power from the MS-9050UD Control Panel. Devices that are using Auxiliary Power from a Power Supply like the FCPS-24FS6 should not be added in this section.
Note on B73: Input any devices that are not included in the battery calculation. Input the part number, quantity, and current draws into the appropriate cells.
Note on B79: Use Circuit Detail Worksheet below for configuring Output Circuits.
Note on H91: Select Standby Time in Hours from the dropdown list.
Note on H94: Select the Alarm Time in minutes from the dropdown list.
Note on H97: Select the Derating Factor from the dropdown list.

## ES-200X
Note 1: You are fully responsible for verifying these calculations. | [10 empty] | Version 10.30.2019
Note 2: Use the dropdowns and the yellow cells to enter values.
ES-200X Battery Calculation
Secondary Power Source Requirements | [11 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[12 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) | [5 empty] | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total |  | 20 Minutes | 0.334 | 72 Hours | 72
Main Circuit Board | 1 | x | 0.141 | = | 0.141 | 1 | x | 0.257 | = | 0.257 |  | 25 Minutes | 0.417 | 90 Hours | 90
IPOTS-COM Communicator | 1 | x | 0.04 | = | 0.04 | 1 | x | 0.041 | = | 0.041 |  | 30 Minutes | 0.5
PWRMOD24 | 0 | x | 0.007 | = |  | 0 | x | 0.008 | = |  |  | 45 Minutes | 0.75
4XTMF | 0 | x | 0.005 | = |  | 0 | x | 0.011 | =
ECC-FFT | 0 | x | 0.12 | = |  | 0 | x | 0.23 | =
CELL-MOD-FL / CELL-CAB | 1 | x | 0.055 | = | 0.055 | 1 | x | 0.1 | = | 0.1
ANN-BUS Devices
ANN-80(-W) | 1 | x | 0.015 | = | 0.015 | 1 | x | 0.04 | = | 0.04
ANN-100 | 0 | x | 0.02 | = |  | 0 | x | 0.025 | =
ANN-LED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
ANN-RLED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
ANN-RLY | 0 | x | 0.015 | = |  | 0 | x | 0.075 | =
ANN-I/O | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
ANN-S/PG | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
Addressable Devices
BEAM355 | 0 | x | 0.002 | =
BEAM355S | 0 | x | 0.002 | =
SD365CO | 0 | x | 0.002
SD355CO | 0 | x | 0.0003 | =
CP355 | 0 | x | 0.0003 | =
SD355 | 0 | x | 0.0003 | =
SD365 | 8 | x | 0.0003 | = | 0.0024
SD355T | 0 | x | 0.0003 | =
SD365T | 0 | x | 0.0002 | =
H355 | 0 | x | 0.0003 | =
H365 | 5 | x | 0.0002 | = | 0.001
H355HT | 0 | x | 0.0003 | =
H365HT | 0 | x | 0.0002 | =
H350R | 0 | x | 0.0003 | =
H355R | 0 | x | 0.0003 | =
H365R | 0 | x | 0.0002 | =
D350RPL | 0 | x | 0.0003 | =
D355PL | 0 | x | 0.0003 | =
MMF-300 | 0 | x | 0.000375 | =
MMF-300-10 | 0 | x | 0.0035 | =
MDF-300 | 0 | x | 0.00075 | =
MMF-301 | 3 | x | 0.00035 | = | 0.00105
MMF-302 | 0 | x | 0.00027 | =
MMF-302-6 | 0 | x | 0.002 | =
BG-12LX | 5 | x | 0.000375 | = | 0.001875
CMF-300 | 0 | x | 0.00039 | =
CMF-300-6 | 0 | x | 0.00225 | =
CRF-300 | 1 | x | 0.000255 | = | 0.000255
CRF-300-6 | 0 | x | 0.00145 | =
CDRM-300 | 0 | x | 0.0013 | =
I300 | 0 | x | 0.0004 | =
ISO-6 | 0 | x | 0.0027 | =
B501BH-2 | 0 | x | 0.001 | =
B501BHT-2 | 0 | x | 0.001 | =
B224RB | 0 | x | 0.0005 | =
B224BI | 0 | x | 0.00045 | =
W-GATE | 0 | x | 0.024 | =
| Maximum alarm draw for all Addressable devices ---------------> | [8 empty] | 0.4
EOLR-1 | 0 | x | 0.02 | = |  | 0 | x | 0.02 | =
FCPS (Remote Sync) | [5 empty] | 0 | x | 0.0217 | =
Resettable Power
4-Wire Smoke Detectors | 0 | x | 0 | = |  | 0 | x | 0 | =
Auxiliary Power
CMF-300 (Aux. Power) | 0 | x | 0.0017 | = |  | 0 | x | 0.007 | =
CMF-300-6 (Aux. Power) | 0 | x | 0.008 | = |  | 0 | x | 0.02 | =
MMF-302 (Aux. Power) | 0 | x | 0.012 | = |  | 0 | x | 0.09 | =
MMF-302-6 (Aux. Power) | 0 | x | 0.05 | = |  | 0 | x | 0.27 | =
B200SR (Aux. Power) | 0 | x | 0.0005 | = |  | 0 | x | 0.035 | =
B200SR-LF (Aux. Power) | 0 | x | 0.001 | = |  | 0 | x | 0.125 | =
SWIFT Wireless
W-GATE | 0 | x | 0.04 | = |  | 0 | x | 0.04 | =
Miscellaneous Devices
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Output Circuits
NAC/Output #1 |  |  | 0 | = |  |  |  | 0.557 | = | 0.557
NAC/Output #2 |  |  | 0 | = |  |  |  | 0 | =
NAC/Output #3 |  |  | 0 | = |  |  |  | 0 | =
NAC/Output #4 |  |  | 0 | = |  |  |  | 0 | =
FCPS (remote Sync) | 0 | x | 0 | = |  | 0 | x | 0.0217 | =
Current Draw from TB3 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.25758 | Total Alarm Load |  |  |  | 1.395
ES-200X Battery Calculation
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.25758 |  |  | x | 24 |  | = | 6.1819
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 1.395 |  |  | x | 0.084 |  | = | 0.11718
Total Current Load | [9 empty] | 6.2991
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 7.5589
Recommended Batteries: | [5 empty] | BAT-12120 - 12AH Batteries
Battery Check
The batteries can be charged by the ES-200X Charger.
The batteries can be housed in the ES-200X Cabinet.
Current Draw Check
NAC#1 current is within the limitations of the circuit.
NAC#2 current is within the limitations of the circuit.
NAC#3 current is within the limitations of the circuit.
NAC#4 current is within the limitations of the circuit.
ES-200X Control Panel:
The output current is within the panel's limitations.
ES-200X Circuit Detail
NAC/Output #1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
SRL 15 | 3 | x | 0 | = | 0 | 3 | x | 0.043 | = | 0.129
P2RL 15 | 1 | x | 0 | = | 0 | 1 | x | 0.054 | = | 0.054
P2RL 110 | 1 | x | 0 | = | 0 | 1 | x | 0.162 | = | 0.162
P2RK110 | 1 | x | 0 | = | 0 | 1 | x | 0.212 | = | 0.212
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0.557
NAC/Output #2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC/Output #3
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC/Output #4
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
Note on J12: If using Reverse Polarity Alarm output, use 0.016; if using the Reverse Polarity Trouble output, use 0.021. Otherwise use 0.011.
Note on B15: NOTE: There cannot be both ANN-BUS Devices and ACS Annunciators connected to the Control Panel. Choose ANN-BUS or ACS NOT both.
Note on B60: Only enter quantities for W-GATE that are being powered on the SLC.
Note on E65: Refer to the Device Compatibility Document for standby current.
Note on B66: Only add those devices that are drawing power from the ES-200X Control Panel. Devices that are using Auxiliary Power from a Power Supply like the FCPS-24FS6 should not be added in this section.
Note on B74: Only enter quantities for W-GATE that are being powered by a Non-Resettable circuit.
Note on B75: Input any devices that are not included in the battery calculation. Input the part number, quantity, and current draws into the appropriate cells.
Note on B81: Use Circuit Detail Worksheet below for configuring Output Circuits.
Note on B87: The total standby current must include both the nonresettable/resettable (TB1 Terminals 1 & 2) and resettable (TB1 Terminals 3 & 4) power. Caution must be taken to ensure that current drawn from these outputs during alarm does not exceed maximum ratings specified. Current limitations of TB3 & TB4 circuits is 2.5 amps per NAC Output and 1.0 amps per special application auxiliary power output.
Note on H96: Select Standby Time in Hours from the dropdown list.
Note on H99: Select the Alarm Time in minutes from the dropdown list.
Note on H102: Select the Derating Factor from the dropdown list.

## MS-9050UD
Note 1: You are fully responsible for verifying these calculations. | [10 empty] | Version 2.19.2018
Note 2: Use the dropdowns in the yellow cells to enter values.
MS-9050UD Battery Calculation
Secondary Power Source Requirements | [11 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[12 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) | [5 empty] | 15 Minutes | 0.25 | 60 Hours | 60
Device | Qty |  | Current Draw |  | Total | Qty |  | Current Draw |  | Total |  | 20 Minutes | 0.334 | 72 Hours | 72
Main Circuit Board | 1 | x | 0.12 | = | 0.12 | 1 | x | 0.2 | = | 0.2 |  | 25 Minutes | 0.417 | 90 Hours | 90
4XTMF | 0 | x | 0.005 | = |  | 0 | x | 0.011 | = |  |  | 30 Minutes | 0.5
EOLR-1 | 0 | x | 0.02 | = |  | 0 | x | 0.02 | = |  |  | 60 Minutes | 1
IPDACT-2 | 0 | x | 0.093 | = |  | 0 | x | 0.136 | =
IPDACT-2UD | 0 | x | 0.098 | = |  | 0 | x | 0.155 | =
ANN-BUS Devices
ANN-SEC Card | 0 | x | 0.003 | = |  | 0 | x | 0.003 | =
ANN-80(-W) | 0 | x | 0.015 | = |  | 0 | x | 0.04 | = |  |  | 90 Minutes | 1.5
ANN-(R)LED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | = |  |  | 180 Minutes | 3
ANN-RLY | 0 | x | 0.015 | = |  | 0 | x | 0.075 | =
ANN-I/O | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
ANN-I/O LED | 0 | x | 0 | = |  | 0 | x | 0.01 | =
ANN-S/PG | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
ANN-LC | 0 | x | 0.15 | = |  | 0 | x | 0.15 | =
Addressable Devices
BEAM355 | 0 | x | 0.002 | =
BEAM355S | 0 | x | 0.002 | =
CP355 | 0 | x | 0.0003 | =
SD355 | 0 | x | 0.0003 | =
SD355T | 0 | x | 0.0003 | =
SD365T | 0 | x | 0.0003 | =
AD355 | 0 | x | 0.0003 | =
H355 | 0 | x | 0.0003 | =
H365 | 0 | x | 0.0003
H355R | 0 | x | 0.0003 | =
H365R | 0 | x | 0.0003 | =
H355HT | 0 | x | 0.0003 | =
H365HT | 0 | x | 0.0003 | =
D350P | 0 | x | 0.0003 | =
D350RP | 0 | x | 0.0003 | =
D350PL | 0 | x | 0.0003 | =
D350RPL | 0 | x | 0.0003 | =
D355PL | 0 | x | 0.0003 | =
MMF-300 | 0 | x | 0.0004 | =
MMF-300-10 | 0 | x | 0.0035 | =
MDF-300 | 0 | x | 0.00075 | =
MMF-301 | 0 | x | 0.000375 | =
MMF-302 | 0 | x | 0.00027 | =
MMF-302-6 | 0 | x | 0.002 | =
BG-12LX | 0 | x | 0.0003 | =
CMF-300 | 0 | x | 0.00039 | =
CMF-300-6 | 0 | x | 0.00225 | =
CRF-300 | 0 | x | 0.00027 | =
CRF-300-6 | 0 | x | 0.00145 | =
CDRM-300 | 0 | x | 0.0013 | =
I300 | 0 | x | 0.0004 | =
ISO-6 | 0 | x | 0.0027 | =
B501BH-2 | 0 | x | 0.001 | =
B501BHT-2 | 0 | x | 0.001 | =
B224RB | 0 | x | 0.0005 | =
B224BI | 0 | x | 0.00045 | =
| Maximum alarm draw for all Addressable devices ---------------> | [8 empty] | 0.4
Resettable Power
4-Wire Smoke Detectors | 0 | x | 0 | = |  | 0 | x | 0 | =
Auxiliary Power
CMF-300 (Aux. Power) | 0 | x | 0.0017 | = |  | 0 | x | 0.007 | =
CMF-300-6 (Aux. Power) | 0 | x | 0.008 | = |  | 0 | x | 0.02 | =
MMF-302 (Aux. Power) | 0 | x | 0.012 | = |  | 0 | x | 0.09 | =
MMF-302-6 (Aux. Power) | 0 | x | 0.05 | = |  | 0 | x | 0.27 | =
B200SR (Aux. Power) | 0 | x | 0.0005 | = |  | 0 | x | 0.035 | =
B200SR-LF (Aux. Power) | 0 | x | 0.001 | = |  | 0 | x | 0.125 | =
Miscellaneous Devices
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Output Circuits
NAC/Output #1 |  |  | 0 | = |  |  |  | 0 | =
NAC/Output #2 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.12 | Total Alarm Load |  |  |  | 0.6
MS-9050UD Battery Calculation
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Total Standby Current |  |  | 0.12 |  |  | x | 24 |  | = | 2.88
Required Alarm Time in Minutes
5 Minutes
Total Alarm Load |  |  | 0.6 |  |  | x | 0.084 |  | = | 0.0504
Total Current Load | [9 empty] | 2.9304
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 3.5165
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
Battery Check
The batteries can be charged by the MS-9050UD Charger.
The batteries can be housed in the MS-9050UD Cabinet.
Current Draw Check
NAC#1 current is within the limitations of the circuit.
NAC#2 current is within the limitations of the circuit.
MS-9050UD current draw:
The required output current is within the panel's limitations
MS-9050UD Circuit Detail
NAC/Output #1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC/Output #2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
Note on B14: NOTE: There cannot be both ANN-BUS Devices and ACS Annunciators connected to the Control Panel. Choose ANN-BUS or ACS NOT both.
Note on E62: Refer to the Device Compatibility Document for standby current.
Note on B63: Only add those devices that are drawing power from the MS-9050UD Control Panel. Devices that are using Auxiliary Power from a Power Supply like the FCPS-24FS6 should not be added in this section.
Note on B70: Input any devices that are not included in the battery calculation. Input the part number, quantity, and current draws into the appropriate cells.
Note on B76: Use Circuit Detail Worksheet below for configuring Output Circuits.
Note on H87: Select Standby Time in Hours from the dropdown list.
Note on H90: Select the Alarm Time in minutes from the dropdown list.
Note on H93: Select the Derating Factor from the dropdown list.

## MS-9200UDLS
Note 1: You are fully responsible for verifying these calculations. | [10 empty] | Version 2.19.2018
Note 2: Use the dropdowns and the yellow cells to enter values.
MS-9200UDLS Battery Calculation
Secondary Power Source Requirements | [11 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[12 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) | [5 empty] | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total |  | 20 Minutes | 0.334 | 72 Hours | 72
Main Circuit Board | 1 | x | 0.145 | = | 0.145 | 1 | x | 0.275 | = | 0.275 |  | 25 Minutes | 0.417 | 90 Hours | 90
XRM-24B | 0 | x | 0 | = |  | 0 | x | 0 | = |  |  | 30 Minutes | 0.5
4XTMF | 0 | x | 0.005 | = |  | 0 | x | 0.011 | = |  |  | 45 Minutes | 0.75
IPDACT-2 | 0 | x | 0.093 | = |  | 0 | x | 0.136 | = |  |  | 60 Minutes | 1
IPDACT-2UD | 0 | x | 0.098 | = |  | 0 | x | 0.155 | =
ECC-FFT | 0 | x | 0.12 | = |  | 0 | x | 0.23 | =
ANN-BUS Devices
ANN-80(-W) | 0 | x | 0.015 | = |  | 0 | x | 0.04 | =
ANN-LED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
ANN-RLED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
ANN-RLY | 0 | x | 0.015 | = |  | 0 | x | 0.075 | =
ANN-I/O | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
ANN-S/PG | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
ANN-LC | 0 | x | 0.15 | = |  | 0 | x | 0.15 | =
ACS Annunciators
ACM-8RF | 0 | x | 0.03 | = |  | 0 | x | 0.158 | =
ACM-16ATF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
ACM-32AF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AEM-16ATF | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
AEM-32AF | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
AFM-16ATF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AFM-32AF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AFM-16AF | 0 | x | 0.025 | = |  | 0 | x | 0.065 | =
LDM-32F | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
LDM-E32F | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
LCD-80F | 0 | x | 0.025 | = |  | 0 | x | 0.064 | =
Addressable Devices
BEAM355 | 0 | x | 0.002 | =
BEAM355S | 0 | x | 0.002 | =
CP355 | 0 | x | 0.0003 | =
SD355 | 0 | x | 0.0003 | =
SD355T | 0 | x | 0.0003 | =
SD365T | 0 | x | 0.0003 | =
AD355 | 0 | x | 0.0003 | =
H355 | 0 | x | 0.0003 | =
H365 | 0 | x | 0.0003
H355R | 0 | x | 0.0003 | =
H365R | 0 | x | 0.0003 | =
H355HT | 0 | x | 0.0003 | =
H365HT | 0 | x | 0.0003 | =
D350P | 0 | x | 0.0003 | =
D350RP | 0 | x | 0.0003 | =
D350PL | 0 | x | 0.0003 | =
D350RPL | 0 | x | 0.0003 | =
D355PL | 0 | x | 0.0003 | =
MMF-300 | 0 | x | 0.0004 | =
MMF-300-10 | 0 | x | 0.0035 | =
MDF-300 | 0 | x | 0.00075 | =
MMF-301 | 0 | x | 0.000375 | =
MMF-302 | 0 | x | 0.00027 | =
MMF-302-6 | 0 | x | 0.002 | =
BG-12LX | 0 | x | 0.0003 | =
CMF-300 | 0 | x | 0.00039 | =
CMF-300-6 | 0 | x | 0.00225 | =
CRF-300 | 0 | x | 0.00027 | =
CRF-300-6 | 0 | x | 0.00145 | =
CDRM-300 | 0 | x | 0.0013 | =
I300 | 0 | x | 0.0004 | =
ISO-6 | 0 | x | 0.0027 | =
B501BH-2 | 0 | x | 0.001 | =
B501BHT-2 | 0 | x | 0.001 | =
B224RB | 0 | x | 0.0005 | =
B224BI | 0 | x | 0.00045 | =
W-GATE | 0 | x | 0.024 | =
| Maximum alarm draw for all Addressable devices ---------------> | [8 empty] | 0.4
EOLR-1 | 0 | x | 0.02 | = |  | 0 | x | 0.02 | =
FCPS (Remote Sync) | [5 empty] | 0 | x | 0.0217 | =
Resettable Power
4-Wire Smoke Detectors | 0 | x | 0 | = |  | 0 | x | 0 | =
Auxiliary Power
CMF-300 (Aux. Power) | 0 | x | 0.0017 | = |  | 0 | x | 0.007 | =
CMF-300-6 (Aux. Power) | 0 | x | 0.008 | = |  | 0 | x | 0.02 | =
MMF-302 (Aux. Power) | 0 | x | 0.012 | = |  | 0 | x | 0.09 | =
MMF-302-6 (Aux. Power) | 0 | x | 0.05 | = |  | 0 | x | 0.27 | =
B200SR (Aux. Power) | 0 | x | 0.0005 | = |  | 0 | x | 0.035 | =
B200SR-LF (Aux. Power) | 0 | x | 0.001 | = |  | 0 | x | 0.125 | =
SWIFT Wireless
W-GATE | 0 | x | 0.04 | = |  | 0 | x | 0.04 | =
W-DIS-D | 0 | x | 0.03 | = |  | 0 | x | 0.03 | =
Miscellaneous Devices
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Output Circuits
NAC/Output #1 |  |  | 0 | = |  |  |  | 0 | =
NAC/Output #2 |  |  | 0 | = |  |  |  | 0 | =
NAC/Output #3 |  |  | 0 | = |  |  |  | 0 | =
NAC/Output #4 |  |  | 0 | = |  |  |  | 0 | =
Current Draw from TB3 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.145 | Total Alarm Load |  |  |  | 0.675
MS-9200UDLS Battery Calculation
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.145 |  |  | x | 24 |  | = | 3.48
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 0.675 |  |  | x | 0.084 |  | = | 0.0567
Total Current Load | [9 empty] | 3.5367
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 4.244
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
Battery Check
The batteries can be charged by the MS-9200UDLS Charger.
The batteries can be housed in the MS-9200UDLS Cabinet.
Current Draw Check
NAC#1 current is within the limitations of the circuit.
NAC#2 current is within the limitations of the circuit.
NAC#3 current is within the limitations of the circuit.
NAC#4 current is within the limitations of the circuit.
MS 9200UDLS Control Panel:
The output current is within the panel's limitations.
MS-9200UDLS Battery Calculation
NAC/Output #1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC/Output #2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC/Output #3
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC/Output #4
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
Note on J11: If using Reverse Polarity Alarm output, use 0.016; if using the Reverse Polarity Trouble output, use 0.021. Otherwise use 0.011.
Note on B15: NOTE: There cannot be both ANN-BUS Devices and ACS Annunciators connected to the Control Panel. Choose ANN-BUS or ACS NOT both.
Note on B23: NOTE: There cannot be both ANN-BUS Devices and ACS Annunciators connected to the Control Panel. Choose ANN-BUS or ACS NOT both.
Note on J24: All eight ACM-8RF relays activated on a single module.
Note on J25: All annunciator LEDs on.
Note on J26: All annunciator LEDs on.
Note on J27: All annunciator LEDs on.
Note on J28: All annunciator LEDs on.
Note on J29: All annunciator LEDs on.
Note on J30: All annunciator LEDs on.
Note on J31: All annunciator LEDs on.
Note on J32: LDM-32F with LEDs on.
Note on B72: Only enter quantities for W-GATE that are being powered on the SLC.
Note on E77: Refer to the Device Compatibility Document for standby current.
Note on B78: Only add those devices that are drawing power from the MS-9200UDLS Control Panel. Devices that are using Auxiliary Power from a Power Supply like the FCPS-24FS6 should not be added in this section.
Note on B86: Only enter quantities for W-GATE that are being powered by a Non-Resettable circuit.
Note on B88: Input any devices that are not included in the battery calculation. Input the part number, quantity, and current draws into the appropriate cells.
Note on B94: Use Circuit Detail Worksheet below for configuring Output Circuits.
Note on B99: The total standby current must include both the nonresettable/resettable (TB1 Terminals 1 & 2) and resettable (TB1 Terminals 3 & 4) power. Caution must be taken to ensure that current drawn from these outputs during alarm does not exceed maximum ratings specified. Current limitations of TB3 & TB4 circuits is 2.5 amps per NAC Output and 1.0 amps per special application auxiliary power output.
Note on H108: Select Standby Time in Hours from the dropdown list.
Note on H111: Select the Alarm Time in minutes from the dropdown list.
Note on H114: Select the Derating Factor from the dropdown list.

## MS-9600LS
Note 1: You are fully responsible for verifying these calculations. | [10 empty] | Version 2.19.2018
Note 2: Use the dropdowns and the yellow cells to enter values.
MS-9600LS Battery Calculation
Secondary Power Source Requirements
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) | [5 empty] | 5 Minutes | 0.084 | 24 Hours | 24
Device Type | Qty |  | Current Draw |  | Total | Qty |  | Current Draw |  | Total |  | 10 Minutes | 0.167 | 48 Hours | 48
Main Circuit Board | 1 | x | 0.103 | = | 0.103 | 1 | x | 0.253 | = | 0.253 |  | 15 Minutes | 0.25 | 60 Hours | 60
DACT-UD2 | 0 | x | 0.017 | = |  | 0 | x | 0.029 | = |  |  | 20 Minutes | 0.334 | 72 Hours | 72
SLC-2LS Expander Module | 0 | x | 0.019 | = |  | 0 | x | 0.026 | = |  |  | 25 Minutes | 0.417 | 90 Hours | 90
4XTMF | 0 | x | 0.005 | = |  | 0 | x | 0.011 | = |  |  | 30 Minutes | 0.5
IPDACT-2 | 0 | x | 0.093 | = |  | 0 | x | 0.136 | = |  |  | 45 Minutes | 0.75
IPDACT-2UD | 0 | x | 0.098 | = |  | 0 | x | 0.155 | = |  |  | 60 Minutes | 1
ANN-BUS Devices
ANN-80(-W) | 0 | x | 0.015 | = |  | 0 | x | 0.04 | =
ANN-LED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
ANN-RLED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
ANN-RLY | 0 | x | 0.015 | = |  | 0 | x | 0.075 | =
ANN-I/O | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
ANN-S/PG | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
ACS Annunciators
ACM-8RF | 0 | x | 0.03 | = |  | 0 | x | 0.158 | =
ACM-16ATF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
ACM-32AF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AEM-16ATF | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
AEM-32AF | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
AFM-16ATF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AFM-32AF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AFM-16AF | 0 | x | 0.025 | = |  | 0 | x | 0.065 | =
LDM-32F | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
LDM-E32F | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
LCD-80F | 0 | x | 0.025 | = |  | 0 | x | 0.064 | =
Resettable Power
4-wire Detector Heads | 0 | x | 0 | = |  | 0 | x | 0 | =
Addressable Devices
BEAM355 | 0 | x | 0.002 | =
BEAM355S | 0 | x | 0.002 | =
CP355 | 0 | x | 0.0003 | =
SD355 | 0 | x | 0.0003 | =
SD355T | 0 | x | 0.0003 | =
SD365T | 0 | x | 0.0003 | =
AD355 | 0 | x | 0.0003 | =
H355 | 0 | x | 0.0003 | =
H365 | 0 | x | 0.0003
H355R | 0 | x | 0.0003 | =
H365R | 0 | x | 0.0003 | =
H355HT | 0 | x | 0.0003 | =
H365HT | 0 | x | 0.0003 | =
D350P | 0 | x | 0.0003 | =
D350RP | 0 | x | 0.0003 | =
D350PL | 0 | x | 0.0003 | =
D350RPL | 0 | x | 0.0003 | =
D355PL | 0 | x | 0.0003 | =
MMF-300 | 0 | x | 0.0004 | =
MMF-300-10 | 0 | x | 0.0035 | =
MDF-300 | 0 | x | 0.00075 | =
MMF-301 | 0 | x | 0.000375 | =
MMF-302 | 0 | x | 0.00027 | =
MMF-302-6 | 0 | x | 0.002 | =
BG-12LX | 0 | x | 0.0003 | =
CMF-300 | 0 | x | 0.00039 | =
CMF-300-6 | 0 | x | 0.00225 | =
CRF-300 | 0 | x | 0.00027 | =
CRF-300-6 | 0 | x | 0.00145 | =
CDRM-300 | 0 | x | 0.0013 | =
I300 | 0 | x | 0.0004 | =
ISO-6 | 0 | x | 0.0027 | =
B501BH-2 | 0 | x | 0.001 | =
B501BHT-2 | 0 | x | 0.001 | =
B224RB | 0 | x | 0.0005 | =
B224BI | 0 | x | 0.00045 | =
W-GATE | 0 | x | 0.024 | =
| Maximum alarm draw for Addressable devices (SLC 1) | [8 empty] | 0.4
| Maximum alarm draw for Addressable devices (SLC 2) | [8 empty] | 0
EOLR-1 | 0 | x | 0.02 | = |  | 0 | x | 0.02 | =
Auxiliary Power
CMF-300 (Aux. Power) | 0 | x | 0.0017 | = |  | 0 | x | 0.007 | =
CMF-300-6 (Aux. Power) | 0 | x | 0.008 | = |  | 0 | x | 0.02 | =
MMF-302 (Aux. Power) | 0 | x | 0.012 | = |  | 0 | x | 0.09 | =
MMF-302-6 (Aux. Power) | 0 | x | 0.05 | = |  | 0 | x | 0.27 | =
B200SR (Aux. Power) | 0 | x | 0.0005 | = |  | 0 | x | 0.035 | =
B200SR-LF (Aux. Power) | 0 | x | 0.001 | = |  | 0 | x | 0.125 | =
SWIFT Wireless
W-GATE | 0 | x | 0.04 | = |  | 0 | x | 0.04 | =
W-DIS-D | 0 | x | 0.03 | = |  | 0 | x | 0.03 | =
Miscellaneous Devices
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Output Circuits
NAC/Output #1 |  |  | 0 | = |  |  |  | 0 | =
NAC/Output #2 |  |  | 0 | = |  |  |  | 0 | =
NAC/Output #3 |  |  | 0 | = |  |  |  | 0 | =
NAC/Output #4 |  |  | 0 | = |  |  |  | 0 | =
Current Draw from TB3 (non-alarm) |  |  | 0 | = |  |  |  | 0 | =
Sum each column for totals | Total Standby Current |  |  |  | 0.103 | Total Alarm Current |  |  |  | 0.653
MS-9600LS Battery Calculation
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current (Amps) |  |  | 0.103 |  |  | x | 24 |  | = | 2.472
Required Alarm Time in Hours
5 Minutes
Alarm Load Current (Amps) |  |  | 0.653 |  |  | x | 0.084 |  | = | 0.054852
Standby and Alarm Load Subtotal | [8 empty] | = | 2.5269
Derating Factor | [8 empty] | = | 1.2
Total Ampere Hours Required | [8 empty] | = | 3.0322
Recommended Batteries: | [5 empty] | BAT-12120 - 12AH Batteries
Battery Check
The batteries can be charged by the MS-9600LS Charger.
The batteries can be housed in the MS-9600LS Cabinet.
Current Draw Check
NAC#1 current is within the limitations of the circuit.
NAC#2 current is within the limitations of the circuit.
NAC#3 current is within the limitations of the circuit.
NAC#4 current is within the limitations of the circuit.
The standby current is within the limitations of the panel.
The alarm current is within output limitations of the panel.
MS-9600LS Circuit Detail
NAC 1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 3
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 4
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
Note on J12: If using Reverse Polarity Alarm output, use 0.016; if using the Reverse Polarity Trouble output, use 0.021. Otherwise use 0.011.
Note on B15: NOTE: There cannot be both ANN-BUS Devices and ACS Annunciators connected to the Control Panel. Choose ANN-BUS or ACS NOT both.
Note on B22: NOTE: There cannot be both ANN-BUS Devices and ACS Annunciators connected to the Control Panel. Choose ANN-BUS or ACS NOT both.
Note on J23: All eight ACM-8RF relays activated on a single module.
Note on J24: All annunciator LEDs on.
Note on J25: All annunciator LEDs on.
Note on J26: All annunciator LEDs on.
Note on J27: All annunciator LEDs on.
Note on J28: All annunciator LEDs on.
Note on J29: All annunciator LEDs on.
Note on J30: All annunciator LEDs on.
Note on J31: LDM-32F with LEDs on.
Note on E35: Refer to the Device Compatibility Document for standby current.
Note on B73: Only enter quantities for W-GATE that are being powered on the SLC.
Note on B77: Only add those devices that are drawing power from the MS-9600LS Control Panel. Devices that are using Auxiliary Power from a Power Supply like the FCPS-24FS6 should not be added in this section.
Note on B85: Only enter quantities for W-GATE that are being powered by a Non-Resettable circuit.
Note on B87: Input any devices that are not included in the battery calculation. Input the part number, quantity, and current draws into the appropriate cells.
Note on B98: The total standby current must include both the resettable (TB3 Terminals 1 & 2) and non-resettable (TB3 Terminals 3 & 4, 5 & 6) power. Caution must be taken to ensure that current drawn from these outputs during alarm does not exceed maximum ratings specified. Current limitations of TB3 circuits is 3.0 amps per output.
Note on H107: Select Standby Time in Hours from the dropdown list.
Note on E108: Value from Total Standby Load cell.
Note on H110: Select the Alarm Time in minutes from the dropdown list.
Note on E111: Value from Alarm Standby Load cell.
Note on L113: Select the Derating Factor from the dropdown list.

## MS-9600UDLS
Note 1: You are fully responsible for verifying these calculations. | [10 empty] | Version 2.19.2018
Note 2: Use the dropdowns and the yellow cells to enter values.
MS-9600UDLS Battery Calculation
Secondary Power Source Requirements
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) | [5 empty] | 5 Minutes | 0.084 | 24 Hours | 24
Device Type | Qty |  | Current Draw |  | Total | Qty |  | Current Draw |  | Total |  | 10 Minutes | 0.167 | 48 Hours | 48
Main Circuit Board | 1 | x | 0.103 | = | 0.103 | 1 | x | 0.253 | = | 0.253 |  | 15 Minutes | 0.25 | 60 Hours | 60
DACT-UD2 | 1 | x | 0.017 | = | 0.017 | 1 | x | 0.029 | = | 0.029 |  | 20 Minutes | 0.334 | 72 Hours | 72
SLC-2LS Expander Module | 0 | x | 0.019 | = |  | 0 | x | 0.026 | = |  |  | 25 Minutes | 0.417 | 90 Hours | 90
4XTMF | 0 | x | 0.005 | = |  | 0 | x | 0.011 | = |  |  | 30 Minutes | 0.5
IPDACT-2 | 0 | x | 0.093 | = |  | 0 | x | 0.136 | = |  |  | 45 Minutes | 0.75
IPDACT-2UD | 0 | x | 0.098 | = |  | 0 | x | 0.155 | = |  |  | 60 Minutes | 1
ANN-BUS Devices
ANN-80(-W) | 0 | x | 0.015 | = |  | 0 | x | 0.04 | =
ANN-LED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
ANN-RLED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
ANN-RLY | 0 | x | 0.015 | = |  | 0 | x | 0.075 | =
ANN-I/O | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
ANN-S/PG | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
ACS Annunciators
ACM-8RF | 0 | x | 0.03 | = |  | 0 | x | 0.158 | =
ACM-16ATF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
ACM-32AF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AEM-16ATF | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
AEM-32AF | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
AFM-16ATF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AFM-32AF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AFM-16AF | 0 | x | 0.025 | = |  | 0 | x | 0.065 | =
LDM-32F | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
LDM-E32F | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
LCD-80F | 0 | x | 0.025 | = |  | 0 | x | 0.064 | =
Resettable Power
4-wire Detector Heads | 0 | x | 0 | = |  | 0 | x | 0 | =
Addressable Devices
BEAM355 | 0 | x | 0.002 | =
BEAM355S | 0 | x | 0.002 | =
CP355 | 0 | x | 0.0003 | =
SD355 | 0 | x | 0.0003 | =
SD355T | 0 | x | 0.0003 | =
SD365T | 0 | x | 0.0003 | =
AD355 | 0 | x | 0.0003 | =
H355 | 0 | x | 0.0003 | =
H365 | 0 | x | 0.0003
H355R | 0 | x | 0.0003 | =
H365R | 0 | x | 0.0003 | =
H355HT | 0 | x | 0.0003 | =
H365HT | 0 | x | 0.0003 | =
D350P | 0 | x | 0.0003 | =
D350RP | 0 | x | 0.0003 | =
D350PL | 0 | x | 0.0003 | =
D350RPL | 0 | x | 0.0003 | =
D355PL | 0 | x | 0.0003 | =
MMF-300 | 0 | x | 0.0004 | =
MMF-300-10 | 0 | x | 0.0035 | =
MDF-300 | 0 | x | 0.00075 | =
MMF-301 | 0 | x | 0.000375 | =
MMF-302 | 0 | x | 0.00027 | =
MMF-302-6 | 0 | x | 0.002 | =
BG-12LX | 0 | x | 0.0003 | =
CMF-300 | 0 | x | 0.00039 | =
CMF-300-6 | 0 | x | 0.00225 | =
CRF-300 | 0 | x | 0.00027 | =
CRF-300-6 | 0 | x | 0.00145 | =
CDRM-300 | 0 | x | 0.0013 | =
I300 | 0 | x | 0.0004 | =
ISO-6 | 0 | x | 0.0027 | =
B501BH-2 | 0 | x | 0.001 | =
B501BHT-2 | 0 | x | 0.001 | =
B224RB | 0 | x | 0.0005 | =
B224BI | 0 | x | 0.00045 | =
W-GATE | 0 | x | 0.024 | =
| Maximum alarm draw for Addressable devices (SLC 1) | [8 empty] | 0.4
| Maximum alarm draw for Addressable devices (SLC 2) | [8 empty] | 0
EOLR-1 | 0 | x | 0.02 | = |  | 0 | x | 0.02 | =
Auxiliary Power
CMF-300 (Aux. Power) | 0 | x | 0.0017 | = |  | 0 | x | 0.007 | =
CMF-300-6 (Aux. Power) | 0 | x | 0.008 | = |  | 0 | x | 0.02 | =
MMF-302 (Aux. Power) | 0 | x | 0.012 | = |  | 0 | x | 0.09 | =
MMF-302-6 (Aux. Power) | 0 | x | 0.05 | = |  | 0 | x | 0.27 | =
B200SR (Aux. Power) | 0 | x | 0.0005 | = |  | 0 | x | 0.035 | =
B200SR-LF (Aux. Power) | 0 | x | 0.001 | = |  | 0 | x | 0.125 | =
SWIFT Wireless
W-GATE | 0 | x | 0.04 | = |  | 0 | x | 0.04 | =
W-DIS-D | 0 | x | 0.03 | = |  | 0 | x | 0.03 | =
Miscellaneous Devices
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Output Circuits
NAC/Output #1 |  |  | 0 | = |  |  |  | 0 | =
NAC/Output #2 |  |  | 0 | = |  |  |  | 0 | =
NAC/Output #3 |  |  | 0 | = |  |  |  | 0 | =
NAC/Output #4 |  |  | 0 | = |  |  |  | 0 | =
Current Draw from TB3 (non-alarm) |  |  | 0 | = |  |  |  | 0 | =
Sum each column for totals | Total Standby Current |  |  |  | 0.12 | Total Alarm Current |  |  |  | 0.682
MS-9600UDLS Battery Calculation
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current (Amps) |  |  | 0.12 |  |  | x | 24 |  | = | 2.88
Required Alarm Time in Hours
5 Minutes
Alarm Load Current (Amps) |  |  | 0.682 |  |  | x | 0.084 |  | = | 0.057288
Standby and Alarm Load Subtotal | [8 empty] | = | 2.9373
Derating Factor | [8 empty] | = | 1.2
Total Ampere Hours Required | [8 empty] | = | 3.5247
Recommended Batteries: | [5 empty] | BAT-12120 - 12AH Batteries
Battery Check
The batteries can be charged by the MS-9600UDLS Charger.
The batteries can be housed in the MS-9600UDLS Cabinet.
Current Draw Check
NAC#1 current is within the limitations of the circuit.
NAC#2 current is within the limitations of the circuit.
NAC#3 current is within the limitations of the circuit.
NAC#4 current is within the limitations of the circuit.
The standby current is within the limitations of the panel.
The alarm current is within output limitations of the panel.
MS-9600UDLS Circuit Detail
NAC 1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 3
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 4
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
Note on J12: If using Reverse Polarity Alarm output, use 0.016; if using the Reverse Polarity Trouble output, use 0.021. Otherwise use 0.011.
Note on B15: NOTE: There cannot be both ANN-BUS Devices and ACS Annunciators connected to the Control Panel. Choose ANN-BUS or ACS NOT both.
Note on B22: NOTE: There cannot be both ANN-BUS Devices and ACS Annunciators connected to the Control Panel. Choose ANN-BUS or ACS NOT both.
Note on J23: All eight ACM-8RF relays activated on a single module.
Note on J24: All annunciator LEDs on.
Note on J25: All annunciator LEDs on.
Note on J26: All annunciator LEDs on.
Note on J27: All annunciator LEDs on.
Note on J28: All annunciator LEDs on.
Note on J29: All annunciator LEDs on.
Note on J30: All annunciator LEDs on.
Note on J31: LDM-32F with LEDs on.
Note on E35: Refer to the Device Compatibility Document for standby current.
Note on B73: Only enter quantities for W-GATE that are being powered on the SLC.
Note on B77: Only add those devices that are drawing power from the MS-9600UDLS Control Panel. Devices that are using Auxiliary Power from a Power Supply like the FCPS-24FS6 should not be added in this section.
Note on B85: Only enter quantities for W-GATE that are being powered by a Non-Resettable circuit.
Note on B87: Input any devices that are not included in the battery calculation. Input the part number, quantity, and current draws into the appropriate cells.
Note on B98: The total standby current must include both the resettable (TB3 Terminals 1 & 2) and non-resettable (TB3 Terminals 3 & 4, 5 & 6) power. Caution must be taken to ensure that current drawn from these outputs during alarm does not exceed maximum ratings specified. Current limitations of TB3 circuits is 3.0 amps per output.
Note on H107: Select Standby Time in Hours from the dropdown list.
Note on E108: Value from Total Standby Load cell.
Note on H110: Select the Alarm Time in minutes from the dropdown list.
Note on E111: Value from Alarm Standby Load cell.
Note on L113: Select the Derating Factor from the dropdown list.