## MRP-2001
MRP-2001 Battery Calculation
Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[11 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) |  |  |  |  | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total | 20 Minutes | 0.334 | 72 Hours | 72
1. System | [10 empty] | 25 Minutes | 0.417 | 90 Hours | 90
Main Circuit Board | 1 | x | 0.095 | = | 0.095 | 1 | x | 0.221 | = | 0.221 | 30 Minutes | 0.5
4XTMF | 0 | x | 0.005 | = |  | 0 | x | 0.011 | = |  | 45 Minutes | 0.75
CAC-5X | 0 | x | 0.001 | = |  | 0 | x | 0.001 | = |  | 60 Minutes | 1
2. Annunciators
ANN-SEC Card | 0 | x | 0.003 | = |  | 0 | x | 0.003 | =
ANN-80(-W) | 0 | x | 0.015 | = |  | 0 | x | 0.04 | =
ANN-RLY | 0 | x | 0.015 | = |  | 0 | x | 0.075 | =
ANN-I/O | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
ANN-I/O LEDs | 0 | x | 0 | = |  | 0 | x | 0.01 | =
ANN-S/PG | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
ANN-(R)LED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
3. Conventional Detectors
IDC Circuits Used Minus 1 | [5 empty] | 0 | x | 0.04 | =
2-Wire Detectors | 0 | x | 0 | =
4-Wire Detectors | 0 | x | 0 | =
4. Other Devices
Power Supervision Relays | 0 | x | 0.025 | = |  | 0 | x | 0.025 | =
Miscellaneous Device 1 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 5 | 0 | x | 0 | = |  | 0 | x | 0 | =
5. Notification Appliances
NAC 1 | [5 empty] | 0 | x | 0 | =
NAC 2 | [5 empty] | 0 | x | 0 | =
NAC 3 | [5 empty] | 0 | x | 0 | =
NAC 4 | [5 empty] | 0 | x | 0 | =
Total Draw from TB9 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.095 | Total Alarm Load |  |  |  | 0.221
MRP-2001 Battery Calculation
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns in the yellow cells to enter values.
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.095 |  |  | x | 24 |  | = | 2.28
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 0.221 |  |  | x | 0.084 |  | = | 0.018564
Total Current Load | [9 empty] | 2.2986
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 2.7583
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
Battery Check
The batteries can be charged by the MRP-2001 Charger.
The batteries can be housed in the MRP-2001 Cabinet.
Current Draw Check
NAC#1 current is within the limitations of the circuit.
NAC#2 current is within the limitations of the circuit.
NAC#3 current is within the limitations of the circuit.
NAC#4 current is within the limitations of the circuit.
MRP-2001 Control Panel:
The output current is within the panel's limitations.
Note on B8: Alarm current shown represents one zone (IDC) on the main circuit board in alarm. One zone consumes 0.040 amps.
Note on B15: Remember to select the number for LED's for each ANN-I/O that is added (Maximum 40 LEDs per ANN-I/O).
Note on B16: Maximum 40 LEDs for each ANN-I/O.
Note on B20: One zone is already taken into account in the Main Circuit Board draw.
Note on H46: Select Standby Time in Hours from the dropdown list.
Note on H49: Select the Alarm Time in minutes from the dropdown list.
Note on H52: Select the Derating Factor from the dropdown list.
Note on J8: Default value: 0.221 Amps. If using the Reverse Polarity Alarm output, use 0.226 amps. If using the Reverse Polarity Trouble output use 0.231 amps.
Note on J9: Default value: 0.011 Amps. If using the Reverse Polarity Alarm output, use 0.016 amps. If using the Reverse Polarity Trouble output use 0.021 amps.

## MRP-2002
MRP-2002 Battery Calculation
Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[11 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) |  |  |  |  | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total | 20 Minutes | 0.334 | 72 Hours | 72
1. System | [10 empty] | 25 Minutes | 0.417 | 90 Hours | 90
Main Circuit Board | 1 | x | 0.095 | = | 0.095 | 1 | x | 0.221 | = | 0.221 | 30 Minutes | 0.5
4XTMF | 0 | x | 0.005 | = |  | 0 | x | 0.011 | = |  | 45 Minutes | 0.75
CAC-5X | 0 | x | 0.001 | = |  | 0 | x | 0.001 | = |  | 60 Minutes | 1
2. Annunciators
ANN-SEC Card | 0 | x | 0.003 | = |  | 0 | x | 0.003 | =
ANN-80(-W) | 0 | x | 0.015 | = |  | 0 | x | 0.04 | =
ANN-RLY | 0 | x | 0.015 | = |  | 0 | x | 0.075 | =
ANN-I/O | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
ANN-I/O LEDs | 0 | x | 0 | = |  | 0 | x | 0.01 | =
ANN-S/PG | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
ANN-(R)LED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
3. Conventional Detectors
IDC Circuits Used Minus 1 | [5 empty] | 0 | x | 0.04 | =
2-Wire Detectors | 0 | x | 0 | =
4-Wire Detectors | 0 | x | 0 | =
4. Other Devices
Power Supervision Relays | 0 | x | 0.025 | = |  | 0 | x | 0.025 | =
Miscellaneous Device 1 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 5 | 0 | x | 0 | = |  | 0 | x | 0 | =
5. Notification Appliances
NAC 1 | [5 empty] | 0 | x | 0 | =
NAC 2 | [5 empty] | 0 | x | 0 | =
NAC 3 | [5 empty] | 0 | x | 0 | =
NAC 4 | [5 empty] | 0 | x | 0 | =
Total Draw from TB9 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.095 | Total Alarm Load |  |  |  | 0.221
MRP-2002 Battery Calculation
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns in the yellow cells to enter values.
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.095 |  |  | x | 24 |  | = | 2.28
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 0.221 |  |  | x | 0.084 |  | = | 0.018564
Total Current Load | [9 empty] | 2.2986
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 2.7583
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
Battery Check
The batteries can be charged by the MRP-2002 Charger.
The batteries can be housed in the MRP-2002 Cabinet.
Current Draw Check
NAC#1 current is within the limitations of the circuit.
NAC#2 current is within the limitations of the circuit.
NAC#3 current is within the limitations of the circuit.
NAC#4 current is within the limitations of the circuit.
MRP-2002 Control Panel:
The output current is within the panel's limitations.
Note on B8: Alarm current shown represents one zone (IDC) on the main circuit board in alarm. One zone consumes 0.040 amps.
Note on B15: Remember to select the number for LED's for each ANN-I/O that is added (Maximum 40 LEDs per ANN-I/O).
Note on B16: Maximum 40 LEDs for each ANN-I/O.
Note on B20: One zone is already taken into account in the Main Circuit Board draw.
Note on H46: Select Standby Time in Hours from the dropdown list.
Note on H49: Select the Alarm Time in minutes from the dropdown list.
Note on H52: Select the Derating Factor from the dropdown list.
Note on J8: Default value: 0.221 Amps. If using the Reverse Polarity Alarm output, use 0.226 amps. If using the Reverse Polarity Trouble output use 0.231 amps.
Note on J9: Default value: 0.011 Amps. If using the Reverse Polarity Alarm output, use 0.016 amps. If using the Reverse Polarity Trouble output use 0.021 amps.