## FCPS-24FS6 & 8
Jobsite Information:
FCPS-24FS6 / 8 Battery Calculation
Entries only to be made in the Yellow cell locations
Regulated Load in Standby
| Number of |  | Current |  | Total Current
Device Type | Devices |  | (Amps) |  | (Amps)
Main PC Board | 1 | X | 0.065 | = | 0.065
Power Supervision Relays |  | X | 0.025 | = | 0
Auxiliary Current Draw |  | X |  | = | 0
from TB4 Terminals 9 & 10
|  |  | STANDBY LOAD | = | 0.065
Regulated Load in ALARM
| Number of |  | Current |  | Total Current
Device Type | Devices |  | (Amps) |  | (Amps)
Main PC Board without AC | 1 | X | 0.145 | = | 0.145
Power Supervision Relays |  | X | 0.025 | = | 0
Auxiliary Current Draw |  | X |  | = | 0
from TB4 Terminals 9 & 10
NAC / Output # 1 |  | X |  | = | 0
NAC / Output # 2 |  | X |  | = | 0
NAC / Output # 3 |  | X |  | = | 0
NAC / Output # 4 |  | X |  | = | 0
|  |  | ALARM LOAD | = | 0.145
Battery Amp Hour Calculation
Standby Load |  |  | Required Standby Time
Current (Amps) |  |  | (Typically 24 or 60 Hours)
| 0.065 | X | 24 | = | 1.56 | AH
Alarm Load |  |  | Required Alarm Time
Current (Amps) |  |  | (Typically 5 or 10 Minutes)
| 0.145 | X | 10 | = | 0.024167 | AH
|  |  |  | Sub Total Standby / Alarm Amp Hours | 1.5842 | AH
|  |  | Multiply by the Derating Factor | X | 1.2 | *
|  |  | Total Ampere Hours Required | = | 2.401 | AH
* Derating Factor required to compensate for the non-linear discharge characteristic of a battery.

## FL-IPKIT
Jobsite Information:
FL-IPKIT Battery Calculation Chart
Entries only to be made in the Yellow cell locations
Regulated Load in Standby
| Number of |  | Current |  | Total Current
Device Type | Devices |  | (Amps) |  | (Amps)
Main PC Board HP300ULX | 1 | X | 0.14 | = | 0.14
IPDACT | 1 | X | 0.1 | = | 0.1
411 | 1 | X | 0.078 | = | 0.078
|  |  | STANDBY LOAD | = | 0.318
Regulated Load in ALARM
| Number of |  | Current |  | Total Current
Device Type | Devices |  | (Amps) |  | (Amps)
Main PC Board without AC | 1 | X | 0.2 | = | 0.2
IPDACT | 1 | X | 0.3 | = | 0.3
411 | 1 | X | 0.126 | = | 0.126
|  |  | ALARM LOAD | = | 0.626
Battery Amp Hour Calculation
Standby Load |  |  | Required Standby Time
Current (Amps) |  |  | (Typically 24 or 60 Hours)
| 0.318 | X | 24 | = | 7.632 | AH
Alarm Load |  |  | Required Alarm Time
Current (Amps) |  |  | (Typically 5 or 10 Minutes)
| 0.626 | X | 5 | = | 0.052167 | AH
|  |  |  | Sub Total Standby / Alarm Amp Hours | 7.6842 | AH
|  |  | Multiply by the Derating Factor | X | 1.2 | *
|  |  | Total Ampere Hours Required | = | 9.721 | AH
* Derating Factor required to compensate for the non-linear discharge characteristic of a battery.
* The HP300ULX is capable of housing batteries up to 12 AH. Batteries larger than 12 AH require a UL listed
external battery cabinet such as the BB-26, BB-55F or other UL listed external battery cabinet.